## Cover
Purpose
Gathering the right data, with the appropriate amount of detail, is a key component to realizing the maximum savings from an energy audit. However, the process for audit data collection is currently non-standardized, and crucial data can be overlooked or the level of detail is insufficient for the required energy and financial analyses. To address these issues, we have created these template data collection forms. The purpose of these sample forms are to assist building energy auditors collect data required to complete comprehensive energy and financial analyses of proposed modifications to the building. These forms are best suited to Level II and Level III audits.
Acknowledgements
Rocky Mountain Institute, Integral Group, Taylor Engineering, kW Engineering
Sample Form Recommended Use
 Identify which of the information listed in these sample forms are needed for your project.
 Identify your anticipated source for each piece of data. Typical data sources are listed below.
 Use the "citation" column where available in case you need to clarify the information at a later time.
 Use the "Guidance" Sample Forms provided that have been filled in sample data as an example of the type of information you should be collecting; you may want to print them out and take them with you to the site.
 Collect as much data as possible prior to a site visit.
 Print the Sample Forms (sometimes multiples of each) and bring them (or the electronic version) with you to the site.
Typical Data Sources
 Facility manager
 As-built drawing sets
 Utility bills
 BAS trend data
 On-site spot measurements
 Temporary logger data
Tools for a Level I Audit : | Tools for a Level II and III Audit :
 Identification |  Illuminance meter (light meter)
 Notebook / Clipboard |  Infrared temperature spot meter
 Phone |  Electronic ballast spinner/detector
 Audit forms appropriate to the site |  Power meter and/or data loggers
 Digital Camera |  Temperature loggers
 Multi-Tool |  Light loggers
 Flashlight |  Motor runtime status loggers
 Digital thermometer and/or humidity meter
 Hearing protection (for mechanical rooms)
Specialized equipment for detailed assessments may also include:
 Boiler stack gas analyzer (for combustion tests)
 Ultrasonic flow meters (for monitoring chilled water, condenser water, or heating water flows
 Infrared camera
 Centralized data logging systems
 Construction hard hat

## TOC
GENERAL INFORMATION
1 | Basics
1.1 | Capital Improvement Plan
1.2 | Utility Cost Data
1.3 | Delivered Consumption Data
1.4 | Preliminary Energy Use Analysis
1.5 | Operations and Maintenance Cost
GEOMETRY &ENVELOPE
2 | Sketches
2.1 | Opaque Surfaces
2.2 | Fenestration
2.3 | Opaque Doors
SCHEDULES
3 | Occupancy
3.1 | Lighting
3.2 | Plug Loads
3.3 | Thermostat Schedule
PEAK LOADS
4 | Peak Occupancy
4.1 | Interior Lighting
4.2 | Exterior Lighting
4.3 | Peak Plug Loads
DOMESTIC HOT WATER
5 | Equipment
5.1 | Fixtures and Use
HVAC & CONTROLS OPTIONS
6 | Boilers
6.1 | Chillers
6.2 | Cooling Towers and Fluid Coolers
6.3 | Pumps and Piping Systems
6.4 | Air Handling System Equipment
6.5 | Air Handling System Controls
6.6 | Air System Terminal Units
6.7 | Zone Heating Equipment
6.8 | Fan Coil Units
6.9 | Exhaust/Return Fans
6.1 | Packaged Units: DX, Heat Pumps
6.11 | Condensing Unit and Condensers
SPECIALTY LOADS SAMPLE FORMS
7 | Swimming Pools
7.1 | Kitchen Equipment
7.2 | Lab Equipment
7.3 | Refrigeration Equipment
7.4 | Datacenters/IT Rooms
7.5 | Process Equipment

## 1.0
Name | Information |  | Citation
Project Name:
Client Name:
City / State:
Building Type: (CBECS if possible)
No. of Stories
Gross Area
Building Age
No. of tenants / Lease type
Key Contacts | Name and position | Phone/Email
Economic Criteria for Energy Projects
Previous Audit Availability
Notes:

## 1.1
To calculate the marginal capital costs of efficiency measures, it is necessary to document any plans for capital improvement. Since a whole-building retrofit may alter the course of almost any type of planned improvements, it is important to document them all (several types are indicated below). Print multiple sheets as necessary.
Capital Improvement Type: (circle one) | HVAC Envelope Electrical Plumbing Aesthetic Life Safety Other
Description of planned replacement, renewal, or system expansion |  | Year Planned | Cost | Citation
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
|  | TOTAL | #VALUE!

## 1.2
Three years of data should be obtained for each meter in the building. If the meter cannot be checked, then obtain utility bills from the client or tenants. Print multiple utility sheets as necessary. | [10 empty] | Three years of data should be obtained for each meter in the building. If the meter cannot be checked, then obtain utility bills from the client or tenants. Print multiple utility sheets as necessary. | [10 empty] | Three years of data should be obtained for each meter in the building. If the meter cannot be checked, then obtain utility bills from the client or tenants. Print multiple utility sheets as necessary.
ELECTRIC | [10 empty] | NATURAL GAS | [10 empty] | OTHER
Utility Name: | [10 empty] | Utility Name: | [10 empty] | Utility Name and Type*:
Account Number: | [10 empty] | Account Number: | [10 empty] | Account Number:
Meter Number: | [10 empty] | Meter Number: | [10 empty] | Meter Number:
Rate Schedule Name: | [10 empty] | Rate Schedule Name: | [10 empty] | Rate Schedule Name:
Notes on Rate: | [10 empty] | Notes on Rate: | [10 empty] | Notes on Rate:
YEAR: | [10 empty] | YEAR: | [10 empty] | YEAR: |  | * Other utilities might be purchased steam, purchased chilled water, LPG, or fuel oil.
| Bill Date | Days in Period | Ave Temp (F) | Actual Demand (kW) | Billed Demand (kW) | Electric Use (kWh) | Demand Cost ($) | Electric Use ($) | Other Fees ($) | Total Bill ($) |  | Bill Date | Days in Period | Ave Temp (F) | Actual Demand* (_______) | Billed Demand* (_______) | Gas Use* (_______) | Demand Cost ($) | Gas Use ($) | Other Fees ($) | Total Bill ($) |  | Bill Date | Days in Period | Ave Temp (F) | Actual Demand* (_______) | Billed Demand* (_______) | Use* (_______) | Demand Cost ($) | Gas Use ($) | Other Fees ($) | Total Bill ($)
January | [9 empty] | 0 | January | [9 empty] | 0 | January | [9 empty] | 0
February | [9 empty] | 0 | February | [9 empty] | 0 | February | [9 empty] | 0
March | [9 empty] | 0 | March | [9 empty] | 0 | March | [9 empty] | 0
April | [9 empty] | 0 | April | [9 empty] | 0 | April | [9 empty] | 0
May | [9 empty] | 0 | May | [9 empty] | 0 | May | [9 empty] | 0
June | [9 empty] | 0 | June | [9 empty] | 0 | June | [9 empty] | 0
July | [9 empty] | 0 | July | [9 empty] | 0 | July | [9 empty] | 0
August | [9 empty] | 0 | August | [9 empty] | 0 | August | [9 empty] | 0
September | [9 empty] | 0 | September | [9 empty] | 0 | September | [9 empty] | 0
October | [9 empty] | 0 | October | [9 empty] | 0 | October | [9 empty] | 0
November | [9 empty] | 0 | November | [9 empty] | 0 | November | [9 empty] | 0
December | [9 empty] | 0 | December | [9 empty] | 0 | December | [9 empty] | 0
[5 empty] | Annual Totals | 0 | 0 | 0 | 0 | 0 | [5 empty] | Annual Totals | 0 | 0 | 0 | 0 | 0 | [5 empty] | Annual Totals | 0 | 0 | 0 | 0 | 0
[11 empty] | * Choose appropriate units for gas (typically MMBtu, MMBtu, therms, or MCF) | [10 empty] | * Units should be whatever appears on the bill
Peak Demand (kW) |  |  | 0 | [7 empty] | Peak Demand (______) |  |  | 0 | [7 empty] | Peak Demand (______) |  |  | 0
Total Annual Cost ($) |  |  | 0 | [7 empty] | Total Annual Cost ($) |  |  | 0 | [7 empty] | Total Annual Cost ($) |  |  | 0
Average kW Cost ($) |  |  | #DIV/0! | [7 empty] | Average _______ Cost ($) |  |  | #DIV/0! | [7 empty] | Average _______ Cost ($) |  |  | #DIV/0!
Average kWh Cost ($) |  |  | #DIV/0! | [7 empty] | Average _______ Cost ($) |  |  | #DIV/0! | [7 empty] | Average _______ Cost ($) |  |  | #DIV/0!

## 1.3
Three years of data should be obtained for each delivered service. Get delivered information from the client or the service provider. Print multiple utility sheets as necessary.
Utility Company:
Account Number:
Rate Number:
Energy Type:
Units:1
Delivery Date | Delivery Amount | Total Cost2
1
2
3
4
5
6
7
8
9
10
11
12 |  |  | Use of Inventory C
13 |  |  |  | At Date 0 |  | A
14 |  |  |  | 365 Days after Date 0 |  | B
15 |  |  |  | Use of Inventory (A-B) | 0 | C
16
17 |  |  | Value of Inventory Used
18 |  |  |  | Latest Price |  | D
19 |  |  |  | Value (CxD) | 0
20
USE OF INVENTORY | C | D
TOTAL CONSUMPTION
1. gal, lbs, etc. | 2. Costs should include tax, fees, contract charges, etc.

## 1.4
Energy Type | Total Annual Use | Units | Conversion Multiplier | Thousands BTU (kBtu) | Total Annual Cost ($)
Electricity |  | MMBtu | 1000 | 0
Natural Gas |  | therms | 100 | 0
Purchased Steam |  |  | 0 | 0
Purchased Hot Water |  |  | 0 | 0
Purchased Chilled Water |  |  | 0 | 0
Oil #_________________ |  |  | 0 | 0
Propane |  |  | 0 | 0
Coal |  |  | 0 | 0
Thermal - On-Site Generated |  |  | 0 | 0
Other |  |  | 0 | 0
Electricity - On-Site Generated |  |  | 0 | 0
Thermal or Electricity - Exported |  |  | 0 | 0
Total |  |  |  | 0 | 0
Gross Conditioned Square Feet
EUI (energy use intensity) | #DIV/0!
Target Finder Score
ECI (energy cost index or $/sf) | #DIV/0!
Notes:
Energy Units | Conversion to kBtu | Notes
kWh | 3.4121
MWh | 3412.142
MMBtu | 1000
therms | 100
dekatherms | 1000
MJ | 0.94782
cubic feet (NG) | 1.027 | 2009 US average, Source 2
MCF (NG) | 1027000
lbs (steam, 15 psig) | 0.94568 | Enthalpy of evaporation only, Source 3
lbs (steam, 50 psig) | 0.91206 | Enthalpy of evaporation only, Source 3
short ton (coal) | 19953 | Source 2
gallons (Fuel Oil #1) | 137.4 | Source 1
gallons (Fuel Oil #2) | 139.6 | Source 1
gallons (Fuel Oil #3) | 141.8 | Source 1
gallons (Fuel Oil #4) | 145.1 | Source 1
gallons (Fuel Oil #5) | 148.8 | Source 1
gallons (Fuel Oil #6) | 152.4 | Source 1
gallons (Diesel) | 139 | Source 1
gallons (Gasoline) | 124 | Source 1
gallons (Propane) | 91.33 | Source 1
cubic feet (Propane) | 2.55 | Source 1
Source 1: | http://www.engineeringtoolbox.com/energy-content-d_868.html
Source 2: | http://www.eia.doe.gov/kids/energy.cfm?page=about_energy_conversion_calculator-basics
Source 3: | http://www.spiraxsarco.com/resources/steam-tables/saturated-steam.asp

## 1.5
Documenting annual operations and maintenance costs will allow you to calculate changes in these costs as a result of the retrofit. If possible, gather at least three years of data. Print additional sheets for each year.
Year: ________
Description | Cost | Citation / Receipt No.
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
TOTAL | #VALUE!

## 2.0
PROFILE SKETCH
This sketch should show a plan view of the building footprint and its surroundings (e.g., adjacent buildings, roadways, water bodies, large trees). Attach site plans or use satellite images if available and mark any changes in layout. Mark the orientation of north and the front or entrance to the building. | This sketch should show a profile view of the building. Attach actual elevations if available. Print multiple sheets as necessary (at least four). Mark dimensions, including floor-to-floor and plenum height.

## 2.1
Use this sheet to describe each major type of opaque surface in the building. Print multiple sheets as necessary.
Surface Name:
Surface type: (circle one) | Exterior Wall Roof Ceiling Floor Interior Wall Slab on Grade Underground Wall
If Slab on Grade or Underground Wall | Slab Total Exposed Perimeter Length: |  | Insulation Type and Thickness:
Perimeter Insulation Depth:
Exterior Solar Reflectivity (%): |  | Interior Surface Reflectance (%): |  | Overall R-Value:
Location(s): (also use Notes below) |  |  |  | No. of Units:
| Description |  |  | Framing
Layer 1 Exterior
Layer 2
Layer 3
Layer 4
Layer 5
Layer 6
Layer 7
Drawings / Notes
Use this space to draw sections, or to make drawings or take notes about opaque surface location.

## 2.2
Use this sheet to describe each type of fenestration in the building. Print multiple sheets as necessary.
Fenestration type: (circle one) | Vertical Overhead |  |  | Angle: (degrees from horizontal)
Location(s): (also use Notes below) |  |  |  | No. of Units:
Type: (circle all that apply) | Fixed Operable Glass door Storefront/Site-built Curtainwall Garden
| Other: (specify) |  |  | Fenestration Age:
| Glazing dimensions: (HxW) |  | Frame Width: | Frame Depth: (used to consider additional glazing)
| Manufacturer: (if applicable) | Name:
Model:
AAMA Product ID:
NFRC Product ID:
Performance: | U-Value |  | SHGC |  | VT
| Center-of-Glass: | Overall Fenestration: | Center-of-Glass: | Overall Fenestration:
Frame Type: (circle one) | Aluminum Aluminum with Thermal Break Wood Vinyl
Wood, Clad with Vinyl/Aluminum Fiberglass Other: (describe)
Frame Condition: | Good Poor Describe: (e.g., leaking)
Glazing Type: (circle all that apply) | Single-glazed Double-glazed Clear Glass Tinted Glass: (describe)
If Skylight: | Curb: Yes No Height: |  | Domed or Flat? Diffuse or Clear?
Interior Shade: (circle one) | None Top Down Bottom Up Other: (describe) |  |  |  | Exterior Shade: Use space below
Drawings / Notes
Use this space to draw any interior or exterior shading (mark dimensions), or to make drawings or take notes about fenestration location.

## 2.3
Use this sheet to describe each type of opaque door in the building. Print multiple sheets as necessary.
Location(s): (also use Notes below) |  |  |  |  | No. of Units:
Type: (circle all that apply) | Swinging Sectional Rolling Site-built |  |  |  | Door Age:
Other: (specify)
Dimensions (HxW):
| Manufacturer: (if applicable) | Name:
Model:
|  | U-Value: | Not including frame: Including frame:
Frame Condition: | Good Poor Describe: |  |  | Frame Material:
Door Condition: | Good Poor Describe: |  |  | Door Material:
Exterior Solar Reflectivity (%): |  |  | Interior Surface Reflectance (%):
Drawings / Notes
Use this space to make drawings or take notes about opaque door location.

## 3.0
Zone Name/Description
Fraction of Peak | Days | M | T | W | TH | F | Sat | Sun | Hol
12-1 am
1-2am
2-3am
3-4am
4-5am
5-6am
6-7am
7-8am
8-9am
9-10am
10-11am
11-12pm
12-1pm
1-2pm
2-3pm
3-4pm
4-5pm
5-6pm
6-7pm
7-8pm
8-9pm
9-10pm
10-11pm
11-12am
Drawings / Notes
Use this space to make drawings or take notes.

## 3.1
Zone Name/Description
Fraction of Peak | Days | M | T | W | TH | F | Sat | Sun | Hol
12-1 am
1-2am
2-3am
3-4am
4-5am
5-6am
6-7am
7-8am
8-9am
9-10am
10-11am
11-12pm
12-1pm
1-2pm
2-3pm
3-4pm
4-5pm
5-6pm
6-7pm
7-8pm
8-9pm
9-10pm
10-11pm
11-12am
Drawings / Notes
Use this space to make drawings or take notes.

## 3.2
Zone Name/Description
Fraction of Peak | Days | M | T | W | TH | F | Sat | Sun | Hol
12-1 am
1-2am
2-3am
3-4am
4-5am
5-6am
6-7am
7-8am
8-9am
9-10am
10-11am
11-12pm
12-1pm
1-2pm
2-3pm
3-4pm
4-5pm
5-6pm
6-7pm
7-8pm
8-9pm
9-10pm
10-11pm
11-12am
Drawings / Notes
Use this space to make drawings or take notes.

## 3.3
Zone Name/ Description:
Heating Set Point: |  | Occupied |  |  | Cooling Set point: |  | Occupied
|  | Unoccupied |  |  |  |  | Unoccupied
Check box to indicate each occupied hour:
Days | M | T | W | TH | F | Sat | Sun | Hol
12-1 am
1-2am
2-3am
3-4am
4-5am
5-6am
6-7am
7-8am
8-9am
9-10am
10-11am
11-12pm
12-1pm
1-2pm
2-3pm
3-4pm
4-5pm
5-6pm
6-7pm
7-8pm
8-9pm
9-10pm
10-11pm
11-12am
Notes

## 4.0
Zone Name/Description:
Peak No. of Full-time Occupants:
Description of Activity Level:
Description of Clothing Insulation Level:
Peak No. of Transient Occupants:
Description of Activity Level:
Description of Clothing Insulation Level:
Zone Watts/SF: | Corresponding Schedule: (Reference Sample Form 1.31)
Drawings / Notes
Use this space to make drawings or take notes.

## 4.1
Use this sheet to describe the electric lighting plan for each zone in your building. Print multiple sheets as necessary.
Zone Name/Description: |  |  |  | Area (SF):
Fixture Manufacturer/Model:
Fixture Type: | Area Task Exit Track Display Other: |  |  | No. of Fixtures:
Mounting: | Recessed Suspended Surface Mount Other: |  |  | No. of Lamps/Fixture:
Lamp Type: | Fluorescent Tube | Length: | Diameter: T12 T8 T5 Other: | Wattage of Lamps:
Circle one: CFL Incandescent Halogen LED HID Other:
Ballast: | Circle one: Magnetic Electronic |  | No. of Ballasts/Fixture: | BF: | Watts:
Control Type: (circle one) | Manual Switch Bi-Level Switch Time Clock Daylight Sensor Occupancy Sensor Dimming StepDimming Other: |  |  | Total Watts:
WorkPlane Height: Horizontal Illuminance: Vertical Illuminance Sensitivity: Lamp Color Temp:
Fixture Manufacturer/Model
Fixture Type: | Area Task Exit Track Display Other: |  |  | No. of Fixtures:
Mounting: | Recessed Suspended Surface Mount Other: |  |  | No. of Lamps/Fixture:
Lamp Type: | Fluorescent Tube | Length: | Diameter: T12 T8 T5 Other: | Wattage of Lamps:
Circle one: CFL Indcandescent Halogen LED HID Other:
Ballast: | Circle one: Magnetic Electronic |  | No. of Ballasts/Fixture: | BF: | Watts:
Control Type: (circle one) | Manual Switch Bi-Level Switch Time Clock Daylight Sensor Occupancy Sensor Dimming StepDimming Other: |  |  | Total Watts:
WorkPlane Height: Horizontal Illuminance: Vertical Illuminance Sensitivity: Lamp Color Temp:
Fixture Manufacturer/Model
Fixture Type: | Area Task Exit Track Display Other: |  |  | No. of Fixtures:
Mounting: | Recessed Suspended Surface Mount Other: |  |  | No. of Lamps/Fixture:
Lamp Type: | Fluorescent Tube | Length: | Diameter: T12 T8 T5 Other: | Wattage of Lamps:
Circle one: CFL Indcandescent Halogen LED HID Other:
Ballast: | Circle one: Magnetic Electronic |  | No. of Ballasts/Fixture: | BF: | Watts:
Control Type: (circle one) | Manual Switch Bi-Level Switch Time Clock Daylight Sensor Occupancy Sensor Dimming StepDimming Other: |  |  | Total Watts:
WorkPlane Height: Horizontal Illuminance: Vertical Illuminance Sensitivity: Lamp Color Temp:
Zone Watts/SF: |  |  | Corresponding Schedule: (Reference Sample Form 1.32)
Notes

## 4.2
Use this sheet to describe the electric lighting plan for the exterior of the building. Print multiple sheets as necessary.
Zone Name/Description |  |  |  | Area (SF):
Manufacturer/Model
Use Type: | Security Advertising ParkingLot ParkingGarage Bldg Façade Landscape Other: |  |  | No. of Fixtures:
Mounting: | Pole Bollard BuildingFacade Ceiling Other |  |  | No. of Lamps/Fixture:
Lamp Type: (circle one) | Flourescent or Neon Tube | Length: | FL Diameter: T12 T10 T8 T5 Neon Diameter (mm): | Wattage of Lamps:
CFL Halogen LED HPS MH MV Other:
Ballast: | Circle one: Magnetic Electronic |  | No. of Ballasts/Fixture: | BF: | Watts:
Control Type: (circle one) | Manual Switch PhotoCell TimeClock PhotoCell/Timeclock MotionSensor Other: |  |  | Total Watts:
Horizontal Illuminance: Vertical Illuminance Sensitivity: Lamp Color Temp:
Manufacturer/Model
Use Type: | Security Advertising ParkingLot ParkingGarage Bldg Façade Landscape Other: |  |  | No. of Fixtures:
Mounting: | Pole Bollard BuildingFacade Ceiling Other |  |  | No. of Lamps/Fixture:
Lamp Type: (circle one) | Flourescent or Neon Tube | Length: | FL Diameter: T12 T10 T8 T5 Neon Diameter (mm): | Wattage of Lamps:
CFL Halogen LED HPS MH MV Other:
Ballast: | Circle one: Magnetic Electronic |  | No. of Ballasts/Fixture: | BF: | Watts:
Control Type: (circle one) | Manual Switch PhotoCell TimeClock PhotoCell/Timeclock MotionSensor Time Clock Other: |  |  | Total Watts:
Horizontal Illuminance: Vertical Illuminance Sensitivity: Lamp Color Temp:
Manufacturer/Model
Use Type: | Security Advertising ParkingLot ParkingGarage Bldg Façade Landscape Other: |  |  | No. of Fixtures:
Mounting: | Pole Bollard BuildingFacade Ceiling Other |  |  | No. of Lamps/Fixture:
Lamp Type: (circle one) | Flourescent or Neon Tube | Length: | FL Diameter: T12 T10 T8 T5 Neon Diameter (mm): | Wattage of Lamps:
CFL Halogen LED HPS MH MV Other:
Ballast: | Circle one: Magnetic Electronic |  | No. of Ballasts/Fixture: | BF: | Watts:
Control Type: (circle one) | Manual Switch PhotoCell TimeClock PhotoCell/Timeclock MotionSensor Time Clock Other: |  |  | Total Watts:
Horizontal Illuminance: Vertical Illuminance Sensitivity: Lamp Color Temp:
Zone Watts/SF: |  |  | Corresponding Schedule: (Reference Sample Form 1.32)
Notes

## 4.3
Use this sheet to describe the electric lighting plan for the exterior of the building. Print multiple sheets as necessary.
Zone Name/Description: |  |  |  | Area (SF):
Manufacturer/Model:
Equipment Type: | Desktop Computer Laptop Printer Fax Other: |  |  | No. of units
Power Draw (kW): |  | If cycling occurs, what is the rate? (e.g. mins per hour) |  | Stand-by power (kW):
Control Type: (circle one) | Occupancy Sensor Other:
Circuit No.
Manufacturer/Model:
Equipment Type: | Desktop Computer Laptop Printer Fax Other: |  |  | No. of units
Power Draw (kW): |  | If cycling occurs, what is the rate? (e.g. mins per hour) |  | Stand-by power (kW):
Control Type: (circle one) | Occupancy Sensor Other:
Circuit No.
Manufacturer/Model:
Equipment Type: | Desktop Computer Laptop Printer Fax Other: |  |  | No. of units
Power Draw (kW): |  | If cycling occurs, what is the rate? (e.g. mins per hour) |  | Stand-by power (kW):
Control Type: (circle one) | Occupancy Sensor Other:
Circuit No.
Zone Watts/SF: |  |  | Corresponding Schedule: (Reference Sample Form 1.33)
Notes

## 5.0
Type: (circle one) | Packaged Storage Water Heater Instantaneous (tankless) Boiler Dishwasher Booster
Purchased Hot Water Purchased Steam Heat Pump Solar Solar Backup Other:_____________
Location(s): |  |  |  |  | No. of Units:
Fuel Type: (circle one) | Natural Gas Electric Fuel Oil LPG Heat recovery Other: __________________________
Manufacturer Information: | Name and Model:
Serial No.:
| Tank Capacity: (if applicable) |  |  | gallons
| Rated Input Capacity: (circle units) |  |  | kBtu/h kW
| Efficiency Rating: (circle units) |  |  | Energy Factor Thermal Efficiency AFUE COP
| Tank Internal Insulation R-Value: (if applicable) |  |  |  | Tank Dimensions:
| Age: (years) |  |  | Condition: (describe)
Does the tank have an external insulation jacket? Yes No What is the R-Value? __________
Average Hot Water Temperature: __________ (°F)
Are the hot water pipes insulated? Yes No How thick? __________
Loop Design Delta T:
Recirculation pump: | Is there a recirculation pump? Yes No |  | Min Flow: (gpm)
| Pump head (ft): |  | Max Flow: (gpm)
| Control (circle one): | Continuous Temperature Timer Demand Other __________
Average recirculation time: (mins)
Drawings / Notes
Use this space to make drawings or take notes about the hot water equipment.

## 5.1
Use this sheet to document the hot water fixtures and their use. This will allow you to calculate hot water heating load reductions resulting from more efficient fixtures.
Type: (circle one) | Lavatory Faucet Kitchen Faucet Dishwasher Laundry Washer
Shower Other: ________________
Location(s): |  |  |  | No. of Units:
Manufacturer Information: | Name and Model:
Serial No.:
| Flow/Cycle Rate: (circle units) |  | GPM: Gallons per Cycle
Age: (years)
Does the fixture leak? Yes No Estimate how much:
Fixture Condition: Good Poor Describe:
Use Rates: (enter information where applicable) | Applicable to:
|  | Cycles per Day: | When do most cycles occur?
| Dishwasher |  | Morning | Mid-day | Evening
Laundry Washer
Shower
|  | Average No. of Users per Day: | When does most use occur?
| Lavatory Faucet Other Fixture |  | Morning | Mid-day | Evening
|  | Average Time of Use per Day: (mins) | When does most use occur?
| Kitchen Faucet Other Fixture |  | Morning | Mid-day | Evening
Drawings / Notes
Use this space to make drawings or take notes about the fixture location or hot water use.

## 6.0
SAMPLE FORM | [7 empty] | SAMPLE FORM GUIDANCE
General Information | [7 empty] | General Information
Site Name: | [7 empty] | Site Name: | Provide name of site
Boiler ID/Tag: | [7 empty] | Boiler ID/Tag: | Near boiler nameplate, as-built boiler schedule
Location/Service: | [7 empty] | Location/Service: | Observe boiler location and area of building it is serving, as-built boiler schedule
Mfr/Model #: | [7 empty] | Mfr/Model #: | Boiler nameplate, as-built boiler submittal
Year Built: |  |  | Serial Number: |  |  |  |  | Year Built: | Boiler nameplate, as-built boiler submittal |  |  | Serial Number: | boiler nameplate
Boiler Type |  |  | Boiler Fuel |  |  | Heating Fluid |  | Boiler Type |  |  | Boiler Fuel |  |  | Heating Fluid
Fire Tube |  |  | Natural Gas |  |  | Water (HWS/HWR) oF |  | Fire Tube | specify boiler type, see as-built boiler submittal |  | Natural Gas | specify boiler fuel used, see as-built boiler submittal |  | Water (HWS/HWR) oF | specify heating fluid type, as well as temperatures or working pressure, see as-built boiler submittal
Water Tube |  |  | Fuel Oil |  |  | Glycol? | yes / no | Water Tube |  |  | Fuel Oil |  |  | Glycol?
Electric |  |  | Propane |  |  | Glycol % |  | Electric |  |  | Propane |  |  | Glycol %
Natural Draft |  |  | Electricity |  |  | Steam psi |  | Natural Draft |  |  | Electricity |  |  | Steam psi
Forced Draft |  |  | Other _________ |  |  | Other _____________ |  | Forced Draft |  |  | Other _________ |  |  | Other
Condensing | [7 empty] | Condensing
Other _________ | [7 empty] | Other _________
Combustion Fan Data |  |  | Design/Measured Data |  |  | Accessories |  | Combustion Fan Data |  |  | Design/Measured Data |  |  | Accessories
Quantity |  |  | Boiler | Design | Measured | Draft Control |  | Quantity | as-built boiler submittal, or visual inspection |  | Boiler | Design | Measured | Draft Control | Check all that apply, see as-built boiler submittal or visual inspection
Manufacturer |  |  | Input/Output (Btu) |  |  | Flue Gas Recirculation |  | Manufacturer |  |  | Input/Output (Btu) | as-built boiler submittal | control system, logger trends, or direct measurement | Flue Gas Recirculation
Full Load hp |  |  | GPM |  |  | Oxygen Trim Control |  | Full Load hp |  |  | GPM* |  |  | Oxygen Trim Control
Frame Size |  |  | WPD (feet) |  |  | Stack Economizer |  | Frame Size |  |  | WPD (feet) |  |  | Stack Economizer
ODP/TEFC |  |  | EWT/LWT (oF) |  |  | Blowdown Economizer |  | ODP/TEFC |  |  | EWT/LWT (oF) |  |  | Blowdown Economizer
Full Load RPM |  |  | Fan | Design | Measured |  |  | Full Load RPM |  |  | Fan
Fan Efficiency |  |  | Volts |  |  | Piping Configuration |  | Fan Efficiency | Enter the fan static efficiency (not the same as motor efficiency), see as-built boiler submittal |  | Volts |  |  | Piping Configuration
Motor Efficiency |  |  | Phase |  |  | Primary-Secondary |  |  |  |  | Phase |  |  | Primary-Secondary | Specify piping configuration, see as-built piping diagram or visual inspection
Full Load Amps |  |  | FLA |  |  | Primary-Only |  |  |  |  | FLA |  |  | Primary-Only
Drive Type |  |  | kW |  |  | Variable Flow |  |  |  |  | kW |  |  | Variable Flow
|  |  | PF |  |  |  |  | Motor Efficiency | as-built boiler submittal, or visual inspection |  | PF
Temperature Control | [7 empty] | Full Load Amps |  |  | *For variable flow systems, enter the maximum flow rate
LWT Setpoint (oF) | [7 empty] | Drive Type
EWT Setpoint (oF)
Reset? | yes / no | If yes, describe: _________ | [5 empty] | Temperature Control
[8 empty] | LWT Setpoint (oF) | Enter boiler leaving water temperature set point if applicable, see as-built sequence of operations
Controls | [7 empty] | EWT Setpoint (oF) | Enter boiler entering water temperature set point if applicable, see as-built sequence of operations
Time of Day Scheduling _____________________________________________________________________ | [7 empty] | Reset? | Indicate whether set point is reset, see as-built sequence of operations
_________________________________________________________________________________________ | [7 empty] | If yes, describe: | Explain reset strategy, see as-built sequence of operations, interview facilities staff
Boiler Staging ____________________________________________________________________________ | [7 empty] | Controls
_________________________________________________________________________________________ | [7 empty] | Time of Day Scheduling |  | Explain boiler scheduling, including lockouts, see as-built sequence of operations, control system, or logger trends.
_________________________________________________________________________________________
[8 empty] | Boiler Staging |  | Explain boiler staging scenario for plants with multiple boilers, see as-built sequence of operations, control system, or logger trends.

## 6.1
SAMPLE FORM |  |  |  |  | SAMPLE FORM GUIDANCE
General Information |  |  |  |  | General Information
Site Name |  |  |  |  | Site Name | provide name of site
Chiller ID/Tag |  |  |  |  | Chiller ID/Tag | near chiller nameplate, as-built chiller schedule
Location/Service |  |  |  |  | Location/Service | observe chiller location and area of building it is serving, as built chiller schedule
Manufacturer/Model # |  |  |  |  | Manufacturer/Model # | chiller nameplate, as-built chiller submittal
Year Built |  | Serial Number |  |  | Year Built | chiller nameplate, as-built chiller submittal |  | Serial Number | chiller nameplate
Chiller Data |  | Design/Operating Conditions |  |  | Chiller Data |  | Design/Operating Conditions
Air or Water Cooled |  |  | Design | Measured | Air or Water Cooled | as-built chiller schedule |  |  | Design | Measured
Refrigerant Type |  | kW/ton @ 100% load |  |  | Refrigerant Type | as-built chiller schedule | kW/ton @ 100% load |  | as-built chiller submittal | control system or logger trends
Piping Arrangement |  | kW/ton @ 50% load |  |  | Piping Arrangement | parallel, series, or primary-secondary for evaporator; and parallel or series for condenser? as-built piping schematic | kW/ton @ 50% load
Chilled Water Glycol | Prop / Eth / None | EER at ARI Conditions |  |  |  |  | NPLV
Glycol % |  | Evap GPM |  |  | Chilled Water Glycol |  | Evap GPM
Capacity (tons) |  | Evap EWT/LWT (oF) |  |  | Glycol % |  | Evap EWT/LWT (oF)
|  | Evap WPD (Ft) |  |  | Capacity (tons) | as-built chiller schedule | Evap WPD (Ft)
Compressor Data |  | Cond GPM |  |  |  |  | Cond GPM
Quantity |  | Cond EWT/LWT (oF) |  |  | Compressor Data |  | Cond EWT/LWT (oF)
Type |  | Cond WPD (Ft) |  |  | Quantity | as-built chiller submittal | Cond WPD (Ft)
RLA |  |  |  |  | Type | as-built chiller submittal
Volts |  | Temperature Control |  |  | RLA | as-built chiller submittal | Temperature Control |  |  | deg F
Phase |  | Cond water supply set point |  |  | Volts | as-built chiller submittal | Cond water supply set point |  |  | as-built sequence of operations
HP |  | Chilled water supply set point |  |  | Phase | as-built chiller submittal | Chilled water supply set point |  |  | as-built sequence of operations
VFD |  | Computerized / Electronic / Pneumatic |  |  | HP | as-built chiller submittal | Computerized / Electronic / Pneumatic |  |  | as-built controls submittal
Compressor Stages |  |  |  |  | VFD | as-built chiller submittal
|  | Condenser Pump Control |  |  | Compressor Stages | as-built chiller submittal | Condenser Pump Control
Condenser Fan Data |  | Pumps Cycled w/Respective Chillers |  | yes / no |  |  | Pumps Cycled w/Respective Chillers |  |  | as-built sequence of operations
Quantity |  | Pumps Operate Independent of Chiller Load |  | yes / no | Condenser Fan Data |  | Pumps Operate Independent of Chillers |  |  | as-built sequence of operations
Manufacturer |  | Pumps Headered / Chiller Headered |  | yes / no | Quantity | as-built chiller submittal | Pumps Headered / Chiller Headered |  |  | as-built sequence of operations
Full Load HP |  | Automatic Isolation Valves |  | yes / no | Manufacturer | as-built chiller submittal | Automatic Isolation Valves |  |  | as-built piping schematic
Frame Size |  | Provide Unusual Piping Arrangement Description/Schematic |  |  | Full Load HP | as-built chiller submittal | Provide Unusual Piping Arrangement Description/Schematic
Enclosure Type |  |  |  |  | Frame Size | as-built chiller submittal
Full Load RPM |  | Evaporator Pump Control |  |  | Enclosure Type | as-built chiller submittal | Evaporator Pump Control
Efficiency |  | Pumps Cycled w/Respective Chillers |  | yes / no | Full Load RPM | as-built chiller submittal | Pumps Cycled w/Respective Chillers |  |  | as-built sequence of operations
Volts |  | Pumps Operate Independent of Chiller Load |  | yes / no | Efficiency | as-built chiller submittal | Pumps Operate Independent of Chillers |  |  | as-built sequence of operations
Phase |  | Pumps Headered / Chillers Headered |  | yes / no | Volts | as-built chiller submittal | Pumps Headered / Chillers Headered |  |  | as-built sequence of operations
Full Load Amps |  | Automatic Isolation Valves |  | yes / no | Phase | as-built chiller submittal | Automatic Isolation Valves |  |  | as-built piping schematic
Service Factor |  | Provide Unusual Piping Arrangement Description/Schematic |  |  | Full Load Amps | as-built chiller submittal | Provide Unusual Piping Arrangement Description/Schematic
Waterside free cooling | yes / no |  |  |  | Service Factor | as-built chiller submittal
[5 empty] | Waterside free cooling | as-built chiller submittal
Controls Notes
Time of Day Scheduling |  |  |  |  | Controls Notes
[5 empty] | Time of Day Scheduling | as-built sequence of operations, control system, or logger trends of chiller kW
[5 empty] | Chiller Sequencing | as-built sequence of operations, control system, or logger trends of chiller kW
Chiller Sequencing

## 6.2
SAMPLE FORM | [5 empty] | SAMPLE FORM GUIDANCE
General Information | [5 empty] | General Information |  | Information Location/Description
Site Name | [5 empty] | Site Name | Enter the name of the building site/campus and building number (if applicable).
Tower ID/Tag | [5 empty] | Tower ID/Tag | Enter the unit identifier, e.g. "CT-1."
Location/Service | [5 empty] | Location/Service | Add any other information that helps identify what the system is serving.
Manufacturer | [5 empty] | Manufacturer | Enter the unit manufacturer. Use nameplate or submittal data.
Model Number |  |  | Serial Number |  |  | Model Number | Enter the unit model number. Use nameplate or submittal data.
Quantity of Cells |  |  | Year Built |  |  | Serial Number | Enter the unit serial number. Use nameplate or submittal data.
[6 empty] | Quantity of Cells | For cooling towers, enter number of individual cells.
Heat Rejection Type |  |  | Fan Data |  |  | Year Built | Enter year of manufacture. Use nameplate or submittal data.
Cooling Tower: |  |  | Fan Control | VFD / Single-speed / Two-Speed
Induced Draft | [5 empty] | Heat Rejection Type | Check whether unit is a cooling tower or fluid cooler, and what type.
Forced Draft |  |  | Fan Drive | Belt / Direct / Gear |  | Piping Arrangement | Primarily applicable to cooling towers. Check arrangement that applies.
Natural Draft |  |  | Fan Type | Centrifugal / Propeller / Other: ______________
Wetted Media | [5 empty] | Fan Control | Circle single-speed, two-speed, or VFD operation. Use nameplate or submittal data.
Fluid Cooler: | [5 empty] | Fan Drive | Circle belt drive, direct drive, or gear drive. Use nameplate or submittal data.
Air Cooled |  |  | Fan Data | Design | Measured | Fan Type | Circle centrifugal or propeller, or enter other type.
Evaporatively Cooled |  |  | Quantity
|  |  | CFM (each fan) |  |  | Fan and Fluid Cooler Pump Data
Piping Arrangement |  |  | Full Load HP |  |  | Qty of fans/pumps | Determine by inspection and enter quantity of fans or pumps.
Basins Headered |  |  | ODP/TEFC |  |  | Fluid Type | Enter the type of fluid that is being cooled. Use submittal or as-built schedule.
Piped to Individ. Chillers |  |  | Full Load RPM |  |  | GPM/CFM | Enter the pump GPM or the fan CFM. Use nameplate or submittal data.
Valves on Supply Headers |  |  | Fan Efficiency |  |  | Manufacturer | Enter unit manufacturer. Use nameplate or submittal data.
|  |  | Motor Efficiency |  |  | Full Load HP | Enter full load horsepower. Use nameplate or submittal data.
Fluid Cooler Pump Data | Design | Measured | Full Load Amps |  |  | ODP/TEFC | Specify motor enclosure: ODP = open drip proof; TEFC = Totally enclosed fan-cooled.
Quantity |  |  | Volts / Phase |  |  | Full Load RPM | Enter motor full load rotational speed. Use nameplate or submittal data.
Fluid Type |  |  | Power Demand (kW) |  |  | Pump/Fan Efficiency | Enter pump or fan static efficiency. Note this is not the same as motor efficiency.
GPM (each pump) |  |  | Power Factor | n/a |  | Motor Efficiency | Enter motor efficiency. Use nameplate or submittal data.
Manufacturer | [5 empty] | Full Load Amps | Enter full load motor current in Amperes. Use nameplate or submittal data.
Full Load HP |  |  | Condenser Water | Design | Measured | Volts/Phase | Enter nominal motor voltage & phase (1 or 3). Use nameplate or submittal data.
ODP/TEFC |  |  | GPM |  |  | Power Demand | Enter full load motor power.
Full Load RPM |  |  | EWT/LWT (oF) |  |  | Power Factor | Enter motor power factor. Use control system or logger trends.
Pump Efficiency |  |  | Ambient DB/WB (oF)
Motor Efficiency | [5 empty] | Condenser Water Data
Full Load Amps |  |  | Basin Heater | Design | Measured | GPM | Enter condenser water flow rate for constant volume systems, and max flow rate for variable flow systems.
Volts / Phase |  |  | Power Demand (kW) |  |  | EWT/LWT | EWT=Temp of water entering condenser/cooling tower; LWT=water temp leaving condenser/tower.
Power Demand (kW) |  |  | Full Load Amps |  |  | Ambient DB/WB | Record current outdoor dry bulb and wet bulb temperatures.
Power Factor | n/a |  | Volts / Phase
|  |  | Power Factor | n/a |  | Basin Heater
[6 empty] | Power Demand | Enter full load heater power.
Controls | [5 empty] | Full Load Amps | Enter full load heater current in Amperes. Use nameplate or submittal data.
Time of Day Scheduling _______________________________________________________________________ | [5 empty] | Volts/Phase | Enter nominal heater voltage & phase (1 or 3). Use nameplate or submittal data.
___________________________________________________________________________________________ | [5 empty] | Power Factor | Enter heater power factor. Use control system or logger trends.
Tower/Cooler Staging ________________________________________________________________________
___________________________________________________________________________________________ | [5 empty] | Controls
Condenser Water Flow Rate ___________________________________________________________________ | [5 empty] | Time of Day Scheduling |  | Describe if unit is on an occupancy schedule, or enabled to run continuously.
___________________________________________________________________________________________ | [5 empty] | Tower/Cooler Staging |  | For systems with multiple units, describe lead/lag, and staging of units.
___________________________________________________________________________________________ | [5 empty] | Condenser Water Flow Rate |  | Describe flow rate control: constant or variable. Use sequence of operation or control system/logger flow rate trends.

## 6.3
SAMPLE FORM GUIDANCE
General Information |  |  |  | General Information
Site Name |  |  |  | Site Name | provide name of site |  |  | Pump Control
Pump ID/Tag |  |  |  | Pump ID/Tag | near fan nameplate, as-built pump schedule |  |  | Constant Volume | as-built sequence of operation
Location/Service |  |  |  | Location/Service | observe pump location/as-built pump schedule |  |  | Variable Volume | as-built sequence of operation
Year Built |  |  |  | Year Built | pump nameplate, as-built pump submittal |  |  | VFD | as-built pump schedule
[8 empty] | Multi-Speed | as-built sequence of operation
Pump Data | Design/Operating Conditions |  |  | Pump Data |  |  |  | Other | as-built sequence of operation
Manufacturer |  | Design | Measured | Manufacturer | pump nameplate, as-built pump schedule |  |  | Connected to DDC? | as-built sequence of operation
Model Number | Total Head (ft. w.g.) |  |  | Model Number | pump nameplate, as-built pump schedule
Serial Number | GPM |  |  | Serial Number | pump nameplate |  |  | Pumping Configuration
Pump Type | Pump Motor RPM |  |  | Pump Type | e.g. end suction, vertical, split case; as-built pump submittal |  |  | Primary Only Variable Flow | as-built sequence of operation, as-built pump schedule, observe VFDs on all pumps
Impeller Size | Volts
Pump Efficiency | Amps |  |  | Impeller Size | pump nameplate, as-built pump schedule |  |  | Primary Only Constant Flow | as-built sequence of operation, as-built pump schedule, observe no VFDs on any pumps
| Power Demand (kW) |  |  | Pump Efficiency | pump nameplate, as-built pump schedule
Pump Motor Data | Power Factor | n/a | [5 empty] | Primary/Secondary Variable Flow | as-built sequence of operation, as-built pump schedule, observe VFDs on secondary pumps only
Full Load HP |  |  |  | Pump Motor Data
Frame Size | Pump Control |  | Notes | Full Load HP | motor nameplate, as-built motor submittal |  |  | Primary/Secondary/ Tertiary | as-built sequence of operation, as-built pump schedule, observe pumps
Enclosure Type | Constant Volume |  | _____________________ | Frame Size | motor nameplate, as-built motor submittal
Full Load RPM | Variable Volume |  | _____________________ | Enclosure Type | motor nameplate, as-built motor submittal |  |  | Other | as-built sequence of operation, as-built pump schedule,
Synch. RPM | VFD |  | _____________________ | Full Load RPM | motor nameplate, as-built motor submittal
Motor Efficiency | Multi-Speed |  | _____________________ | Synch. RPM | motor nameplate, as-built motor submittal
Volts | Other |  | _____________________ | Motor Efficiency | motor nameplate, as-built motor submittal |  |  | Miscellaneous Accessories
Phase | Connected to DDC? | Yes/No | _____________________ | Volts | motor nameplate, as-built motor submittal |  |  | Suction Diffusers | observe piping system; as-built plumbing drawings
Full Load Amps |  |  |  | Phase | motor nameplate, as-built motor submittal |  |  | Triple Duty Valves
Connection Type |  |  |  | Full Load Amps | motor nameplate, as-built motor submittal |  |  | Throttling Valves
|  |  |  | Drive Type | as-built fan schedule, as-built fan submittal |  |  | Circuit Setters
Pumping Configuration | Miscellaneous Accessories | [6 empty] | Other
Primary Only Variable Flow | Suction Diffusers |  |  | Design/Operating Conditions
Primary Only Constant Flow | Triple Duty Valves |  |  |  | Design |  |  | Measured
Primary/Secondary Variable | Throttling Valves |  |  | Total Head | as-built pump schedule |  | Test and Balance report
Primary/Secondary/Tertiary | Circuit Setters |  |  | GPM | as-built pump schedule |  | building control system or logger trends
Other _________________ | Other _____________ |  |  | Pump Motor RPM | as-built pump schedule |  | building control system or logger trends
|  |  |  | Volts | as-built pump schedule |  | building control system or logger trends
Controls Notes |  |  |  | Amps | as-built pump schedule |  | building control system or logger trends
Time of Day Scheduling |  |  |  | Power Demand | as-built pump schedule |  | building control system or logger trends
|  |  |  | Power Factor | n/a |  | building control system or logger trends
Controls Notes
|  |  |  | Time of Day Scheduling |  | as-built sequence of operation, control system or logger trends of pump speed (or Amps or kW)
Pump Staging |  |  |  | Pump Staging |  | as-built sequence of operation, control system or logger trends of pump speed (or Amps or kW)

## 6.4
SAMPLE FORM |  |  |  |  | SAMPLE FORM GUIDANCE
General Information |  |  |  |  | General Information |  |  | Fan Configuration
Site Name |  |  |  |  | Site Name | provide name of site |  | Blow or Draw-thru | as-built AHU schedule
Air Handler ID/Tag |  |  |  |  | Air Handler ID/Tag | near AHU nameplate, as-built AHU schedule
Location/Service |  |  |  |  | Location/Service | observe fan location/as-built AHU schedule |  | Return Air Path
Manufacturer/Model # |  |  |  |  | Manufacturer/Model # | AHU nameplate, as-built AHU submittal |  | Ducted or Plenum | as-built ductwork plan
Year Built |  |  | Serial Number |  | Year Built/Serial Number | AHU nameplate, as-built AHU submittal
Humidifier
Supply Fan Data |  |  | Fan Configuration |  | Supply Fan Data |  |  | Type | electric, steam, or adiabatic; as-built humidifier schedule
Manufacturer |  |  | Blow-thru |  | Manufacturer | AHU nameplate, as-built AHU schedule
Model Number |  |  | Draw-thru |  | Model Number | AHU nameplate, as-built AHU schedule |  | Capacity (lbs/hr) | as-built AHU schedule
Serial Number |  |  |  |  | Serial Number | AHU nameplate
Fan Type / Size |  |  | Return Air Path |  | Fan Type / Size | AHU nameplate, as-built AHU schedule |  | Cooling Coil
Fan Efficiency |  |  | Ducted |  | Fan Efficiency | AHU nameplate, as-built AHU schedule |  | Chilled Water | as-built AHU schedule
|  |  | Plenum |  |  |  |  | Sens/Lat Capacity | as-built AHU schedule
Supply Fan Motor Data |  |  |  |  | Supply Fan Motor Data |  |  | Design CFM/GPM | as-built AHU schedule
Full Load HP |  |  | Humidifier |  | Full Load HP | motor nameplate, as-built motor submittal |  | Design EDB/EWB | as-built AHU schedule
Frame Size |  |  | Type |  | Frame Size | motor nameplate, as-built motor submittal |  | Design LDB/LWB | as-built AHU schedule
Enclosure Type |  |  | Capacity (lbs/hr) |  | Enclosure Type | motor nameplate, as-built motor submittal |  | Design EWT/LWT | as-built AHU schedule
Full Load RPM |  |  |  |  | Full Load RPM | motor nameplate, as-built motor submittal |  | Meas EWT/LWT | control system or logger trends
Synch. RPM |  |  | Cooling Coil | NONE | Synch. RPM | motor nameplate, as-built motor submittal |  | Air Pressure Drop | as-built AHU schedule
Motor Efficiency |  |  | Chilled Water (2 Way/3 Way Valve) |  | Motor Efficiency | motor nameplate, as-built motor submittal
Volts |  |  | Sensible/Latent Capacity |  | Volts | motor nameplate, as-built motor submittal |  | Heating Coil
Phase |  |  | Design CFM / GPM |  | Phase | motor nameplate, as-built motor submittal |  | Medium Type | water, steam, or electric
Full Load Amps |  |  | Design EDB / EWB |  | Full Load Amps | motor nameplate, as-built motor submittal |  | Capacity (MBTUH) | as-built AHU schedule
Motor In Supply Airstream? | Yes/No |  | Design LDB / LWB |  | Motor In Supply Airstream? | motor nameplate, as-built motor submittal |  | Design CFM/GPM | as-built AHU schedule
Drive Type |  |  | Design EWT / LWT |  | Drive Type | as-built fan schedule, as-built fan submittal |  | Design EDB/LDB | as-built AHU schedule
|  |  | Measured EWT / LWT |  |  |  |  | Design EWT/LWT | as-built AHU schedule
Supply Fan Design/Operating Conditions |  |  | Air Pressure Drop |  | Pre-Heat Coil |  |  | Meas EWT/LWT | control system or logger trends
| Design | Measured |  |  | Medium Type | water, steam, or electric
Total Static Pressure |  |  | Pre-Heat Coil | NONE | Capacity (MBTUH) | as-built AHU schedule |  | Filter Data
Occupied CFM |  |  | Medium Type |  | Design CFM / GPM | as-built AHU schedule |  | Manufacturer | nameplate; as-built submittal
Unoccupied CFM |  |  | Capacity (MBTUH) |  | Design EDB / LDB | as-built AHU schedule |  | Model Number | nameplate; as-built submittal
Fan RPM |  |  | Design CFM / GPM |  | Design EWT / LWT | as-built AHU schedule |  | Type | nameplate; as-built submittal
Volts |  |  | Design EDB / LDB |  | Measured EWT / LWT | control system or logger trends |  | Efficiency | nameplate; as-built submittal
Occupied Amps |  |  | Design EWT / LWT |  |  |  |  | Initial/Final PD | as-built submittal
Unoccupied Amps | n/a |  | Measured EWT / LWT |  | Supply Fan Design/Operating Conditions
Occupied kW | [5 empty] | Design |  | Measured
Unoccupied kW | n/a |  | Heating Coil | NONE | Total Static Pressure | as-built AHU schedule | Test and Balance report
Power Factor | n/a |  | Medium Type |  | Occupied CFM | basis of design, as-built sequence of operation | building control system or logger trends
|  |  | Capacity (MBTUH) |  | Unoccupied CFM | basis of design, as-built sequence of operation | building control system or logger trends
Filter Data |  |  | Design CFM / GPM |  | Fan RPM | as-built fan schedule | building control system or logger trends
Manufacturer |  |  | Design EDB / LDB |  | Volts | as-built fan schedule | building control system or logger trends
Model Number |  |  | Design EWT / LWT |  | Occupied Amps | as-built fan schedule | building control system or logger trends
Type |  |  | Measured EWT / LWT |  | Unoccupied Amps | n/a | building control system or logger trends
Efficiency |  |  |  |  | Occupied kW | as-built fan schedule | building control system or logger trends
Initial/Final Pressure Drop |  |  |  |  | Unoccupied kW | n/a | building control system or logger trends
[5 empty] | Power Factor | n/a | building control system or logger trends

## 6.5
SAMPLE FORM |  |  |  |  | SAMPLE FORM GUIDANCE
General Information |  |  |  |  | General Information
Site Name |  |  |  |  | Site Name | provide name of site
Air Handler ID/Tag |  |  |  |  | Air Handler ID/Tag | near AHU nameplate, as-built AHU schedule
Location/Service |  |  |  |  | Location/Service | observe fan location/as-built AHU schedule
Manufacturer/Model # |  |  |  |  | Manufacturer/Model # | AHU nameplate, as-built AHU submittal
Year Built |  | Serial Number |  |  | Year Built | AHU nameplate, as-built AHU submittal | Serial Number | AHU nameplate
Supply Fan Control |  | Outside Air (OA) Control |  |  | Supply Fan Control |  | Outside Air (OA) Control
Constant Air Volume |  | Fixed OA CFM |  |  | Constant Air Volume | as-built sequence of operation | Fixed OA CFM | as-built sequence of operation
VFD |  | Economizer? | Yes/No |  | VFD | as-built sequence of operation | Economizer? | as-built sequence of operation, control system trends of economizer damper position
Discharge Damper |  | Minimum OA % |  |  | Discharge Damper | as-built sequence of operation
Multi-Speed |  | Economizer Control |  |  | Multi-Speed | as-built sequence of operation | Minimum OA % | as-built sequence of operation, as-built AHU schedule
DDC |  | Econo Upper Limit |  |  | DDC | as-built sequence of operation
Electronic Controls |  | Econo Lower Limit |  |  | Electronic Controls | as-built sequence of operation | Economizer Control | e.g. drybulb, RH, enthalpy; as-built sequence of operation, control system trends
Pneumatic Controls |  | Econo Control Point |  |  | Pneumatic Controls | as-built sequence of operation
Room Thermostat |  |  |  |  | Room Thermostat | as-built sequence of operation | Econo Upper Limit | e.g. upper OA drybulb temp lockout; as-built sequence of operation, control system trends
Humidifier Control |  | Temperature Control |  |  | Supply Fan Static Pressure (SP) Control |  | Econo Lower Limit | e.g. lower OA drybulb temp lockout; as-built sequence of operation, control system trends
Humidity Control? | Yes/No | Occupied Room Temperature Setpoint |  |  | Constant SP Setpoint | as-built sequence of operation
Humidity Sensor Location |  | Unoccupied Room Temperature Setpoint |  |  | Static Pressure Reset | as-built sequence of operation | Econo Control Point | e.g. MA temp, CO2 sensor, as-built sequence of operation
RH Setpoint, Max |  | Heating Supply Air Temperature Setpoint
RH Setpoint, Min |  | Cooling Supply Air Temperature Setpoint
|  | Supply Air Temperature Setpoint Reset |  | Yes/No | Humidifier Control |  | Temperature Control
[5 empty] | Humidity Control? | as-built sequence of operation | Occ Room Temp | control system or logger trends
Operating Schedule |  | Supply Fan Static Pressure Control |  |  | Humidity Sensor Location | as-built sequence of operation, visual observation | Unocc Room Temp | control system or logger trends
Occupied Hours |  | Constant Static Pressure Setpoint |  |  |  |  | Heating SAT | control system or logger trends
Unoccupied Hours |  | Static Pressure Reset |  |  | RH Setpoint, Max | %, as-built sequence of operation, control system or logger trends | Cooling SAT | control system or logger trends
Morning Warm-Up Hours | [6 empty] | SAT Setpoint Reset | control system or logger trends
[5 empty] | RH Setpoint, Min | %. as-built sequence of operation, control system or logger trends
Ductwork Control Accessories |  | Louver/Damper Control
Turning Vanes? |  | Location(s)
Single / Dual Duct |  | % Free Area |  |  | Operating Schedule
Other ________________ |  | Pressure Drop |  |  | Occupied Hours | Specify occupied hours for each day of the week; as-built sequence of operation
|  | Control Method |  |  | Unoccupied Hours | Specify unoccupied hours for each day of the week; as-built sequence of operation
[5 empty] | Morning Warm-Up Hours | Specify when air handling system turn on for pre-occupancy warm-up for each day of the week; as-built sequence of operation, control system trends of supply fan speed and supply air temperature
Controls Notes |  |  |  |  | Ductwork Control Accessories |  | Louver/Damper Control
[5 empty] | Turning Vanes? | observe duct interiors; as-built ductwork plan | Location(s) | observe; as-built ductwork plan
[5 empty] | Single / Dual Duct | as-built ductwork plan | % Free Area | measure; as-built ductwork plan
[5 empty] | Other | as-built ductwork plan | Pressure Drop | measure; as-built ductwork plan
[7 empty] | Control Method | as-built sequence of operation

## 6.6
SAMPLE FORM | [10 empty] | SAMPLE FORM GUIDANCE
General Information | [10 empty] | General Information
Site Name: | [10 empty] | Site Name: |  | Provide name of site
Location/Service: | [10 empty] | Location/Service: |  | Provide information to identify what the system is serving, observe and see as-built equipment schedule
Terminal Units | [10 empty] | Terminal Units
AHU/Source | Tag/I.D. | Mfr./ Model # | Type | Max. CFM | Htg. Min. CFM | Clg. Min. CFM | Heat Source | Cool Source | Control Type | Notes | AHU/Source | Enter/identify the equipment from which the air originates before supplying the terminal unit. See as-built floor plans.
[11 empty] | Tag/ID | Enter the terminal unit identifier, e.g. "VAV-27," if applicable, see nameplate or as-built equipment schedule
[11 empty] | Mfr./Model # | Enter the manufacturer and model number of the terminal unit, see nameplate or as-built equipment submittal
[11 empty] | Type | Enter the following indicators of terminal unit type: VAV=Variable Air Volume Terminal Unit CAV=Constant Air Volume Terminal Unit FPB=Fan-Powered Box (provide fan specs in notes section) Other=Explain in notes section
[11 empty] | Max CFM | For CAV and FPB, enter CFM. For VAV, enter maximum CFM. Provide source in notes section (measured, TAB report, drawings, etc.)
[11 empty] | Heating Min | For VAV only. Enter minimum heating CFM (provide source in Notes section)
[11 empty] | Cooling Min | For VAV only. Enter minimum cooling CFM (provide source in Notes section)
[11 empty] | Heat Source | Enter the source of heating, see as-built equipment schedule and floor plans. (e.g. if hot water reheat coil, give source of hot water, e.g. "Boiler #1."; If eclectic resistance reheat coil, enter "elec")
[11 empty] | Cool Source | Enter the source of cooling, see as-built equipment schedule and floor plans. If cooling occurs in central AHU, enter "None." If chilled water coil in terminal unit, enter 'CHW.' If DX cooling coil in terminal unit enter 'DX'.
[11 empty] | Control Type | For digital thermostat, enter "D-T." For on/off control enter "on/off" For other, enter "other" and explain in Notes Section
[11 empty] | Notes | Use this space to enter any additional notes or comments including those stated above.

## 6.7
SAMPLE FORM | [8 empty] | SAMPLE FORM GUIDANCE
General Information | [8 empty] | General Information
Site Name | [8 empty] | Site Name |  | provide name of site
Heating Equip. ID/Tag | [8 empty] | Heating Equip. ID/Tag |  | near equipment nameplate, as-built equipment schedule
Location/Service | [8 empty] | Location/Service |  | observe location and equipment it is serving, as built equipment schedule
Manufacturer/Model # | [8 empty] | Manufacturer/Model # |  | equipment nameplate, as-built equipment submittal
Year Built |  |  |  | Serial Number |  |  |  |  | Year Built |  | nameplate, or as-built submittal |  |  |  | Serial Number | nameplate
Room Conditions | [8 empty] | Room Conditions
Air Delivery Sys Type | [8 empty] | Air Delivery Sys Type |  | basis of design, as-built floor plans
Actual Room Temp. | [8 empty] | Actual Room Temp. |  | control system or logger trends
Room Temp Set Point (htg) | [8 empty] | Room Temp Set Point (htg) |  | basis of design or control system
Equipment Data | Radiator | Convector | Furnace | Infrared Heater | Radiant Panel | Radiant Slab | Chilled Beam | Other | Equipment Data | Radiator | Convector | Furnace | Infrared Heater | Radiant Panel | Radiant Slab | Chilled Beam | Other
Quantity | [8 empty] | Quantity | Observe actual quantity, also see as-built equipment schedules
Medium | [8 empty] | Medium | as-built equipment submittal
Dimensions | [8 empty] | Dimensions | Observe actual dimensions, also see as-built equipment submittal
Material | [8 empty] | Material | as-built equipment submittal
Capacity | [8 empty] | Capacity | as-built equipment submittal
Design Flow rate | [8 empty] | Design Flow rate | as-built equipment schedule
Meas. Flow rate | [8 empty] | Meas. Flow rate | control system or logger trends
Design SAT | [8 empty] | Design SAT | as-built equipment schedule
Meas. SAT | [8 empty] | Meas. SAT | control system or logger trends
Design EWT | [8 empty] | Design EWT | as-built equipment schedule
Meas. EWT | [8 empty] | Meas. EWT | control system or logger trends
Design Pd | [8 empty] | Design Pd | as-built equipment schedule
Meas. Pd | [8 empty] | Meas. Pd | control system or logger trends
Condensing/Non | [8 empty] | Condensing/Non | as-built equipment submittal
Combustion Method | [8 empty] | Combustion Method | as-built equipment submittal
MUA required | [8 empty] | MUA required | as-built equipment submittal
Thermal Efficiency | [8 empty] | Thermal Efficiency | as-built equipment submittal
Stages | [8 empty] | Stages | as-built equipment submittal
Volts | [8 empty] | Volts | as-built equipment schedule
Design Amps | [8 empty] | Design Amps | as-built equipment schedule
Meas. Amps | [8 empty] | Meas. Amps | control system or logger trends
Design kW | [8 empty] | Design kW | as-built equipment schedule
Measured kW | [8 empty] | Measured kW | control system or logger trends
Power Factor | [8 empty] | Power Factor | control system or logger trends
Note: Not all data categories apply to every zone heating equipment type!!
Controls Notes
Operating Schedule | [8 empty] | Controls Notes
[9 empty] | Operating Schedule | As-Built sequence of operation, observe at least one week of control system trends of equipment status, or use data logger to monitor equipment power consumption for at least one week
Method of Control (Tstat, occ. Sensor, etc.)
[9 empty] | Method of Control (Tstat, occ. Sensor, etc.) |  |  | as-built sequence of operation, as-built floor plans

## 6.8
SAMPLE FORM |  |  |  |  | SAMPLE FORM GUIDANCE
General Information |  |  |  |  | General Information
Site Name |  |  |  |  | Site Name | provide name of site
Fan Coil ID/Tag |  |  |  |  | Fan Coil ID/Tag | near FCU nameplate, as-built FCU schedule
Location/Service |  |  |  |  | Location/Service | observe FCU location and equipment it is serving, as built FCU schedule
Manufacturer/Model # |  |  |  |  | Manufacturer/Model # | FCU nameplate, as-built FCU submittal
Year Built |  | Serial Number |  |  | Year Built | FCU nameplate, or as-built FCU submittal | Serial Number | FCU nameplate
Room Conditions |  | Cooling Coil Data |  |  | Room Conditions |  | Cooling Coil Data
Air Delivery Sys Type |  |  | Design | Measured | Air Delivery Sys Type | basis of design, as-built floor plans |  | Design | Measured
Actual Room Temperature |  | Medium Type |  |  | Actual Room Temperature | control system or logger trends | Medium Type | as-built FCU schedule
Room Temp Setpoint (htg) |  | 2-Way / 3-Way Valve |  |  | Room Temp Setpoint (htg) | basis of design or control system | 2-Way / 3-Way Valve | as-built FCU controls diagram
Room Temp Setpoint (clg) |  | Sensible/Total Capacity |  |  | Room Temp Set Point (clg) | basis of design or control system | Sensible/Total Cap. | as-built FCU schedule
RH Setpoint |  | CFM |  |  | RH Set Point | basis of design or control system | CFM | as-built FCU schedule | control system or logger trends
|  | EDB/WB |  |  |  |  | EDB/WB
Fan Data |  | LDB/WB |  |  | Fan Data |  | LDB/WB
Fan Type/Size |  | EWT |  |  | Fan Type/Size | as-built FCU or filter schedule/submittal | EWT
Fan Efficiency |  | LWT |  |  | Fan Efficiency | as-built FCU or filter schedule/submittal | LWT
|  | Air Pressure Drop |  |  |  |  | Air Pressure Drop | as-built FCU schedule
Fan Motor Data |  | Water Pressure Drop |  |  | Fan Motor Data |  | Water Pressure Drop | as-built FCU schedule
Full Load HP |  |  |  |  | Full Load HP | motor nameplate, as-built motor submittal
Frame Size |  | Heating Coil Data |  |  | Frame Size | motor nameplate, as-built motor submittal | Heating Coil Data
Enclosure Type |  | Medium Type |  |  | Enclosure Type | motor nameplate, as-built motor submittal | Medium Type | as-built FCU schedule
Full Load RPM |  | 2-Way / 3-Way Valve |  |  | Full Load RPM | motor nameplate, as-built motor submittal | 2-Way / 3-Way Valve | as-built FCU controls diagram
Synch. RPM |  | Capacity |  |  | Synch. RPM | motor nameplate, as-built motor submittal | Capacity | as-built FCU schedule
Motor Efficiency |  | CFM |  |  | Motor Efficiency | motor nameplate, as-built motor submittal | CFM | as-built FCU schedule | control system or logger trends
Volts |  | EDB |  |  | Volts | motor nameplate, as-built motor submittal | EDB
Phase |  | LDB |  |  | Phase | motor nameplate, as-built motor submittal | LDB
Full Load Amps |  | EWT |  |  | Full Load Amps | motor nameplate, as-built motor submittal | EWT
Motor In Supply Airstream? | Yes/No | LWT |  |  | Motor In Supply Airstream? | motor nameplate, as-built motor submittal | LWT
Drive Type |  | Air Pressure Drop |  |  | Drive Type | as-built FCU schedule, as-built FCU submittal | Air Pressure Drop | as-built FCU schedule
|  | Water Pressure Drop |  |  |  |  | Water Pressure Drop | as-built FCU schedule
Filter Data |  |  |  |  | Filter Data
Manufacturer |  | Fan Design/Operating Conditions |  |  | Manufacturer | as-built FCU or filter schedule/submittal | Fan Design/Operating Conditions
Model Number |  | Total Static Pressure |  |  | Model Number | as-built FCU or filter schedule/submittal | Total Static Pressure | as-built FCU schedule | TAB report
Type |  | Airflow |  |  | Type | as-built FCU or filter schedule/submittal | Airflow |  | control system or logger trends
Efficiency |  | Fan RPM |  |  | Efficiency | as-built FCU or filter schedule/submittal | Fan RPM
Initial / Final Pressure Drop |  | Volts |  |  | Initial / Final Pressure Drop | as-built FCU or filter schedule/submittal | Volts
|  | Amps |  |  |  |  | Amps
Fan Controls |  | kW |  |  | Fan Controls |  | kW
Constant Air Volume |  | Power Factor | n/a |  | Constant Air Volume | as-Built sequence of operation | Power Factor | n/a
VFD |  |  |  |  | VFD | as-Built sequence of operation
Discharge Damper |  | Operating Schedule |  | Notes | Discharge Damper | as-Built sequence of operation | Operating Schedule
Multi-Speed |  | Thermostat |  |  | Multi-Speed | as-Built sequence of operation | Thermostat | As-Built sequence of operation, observe at least one week of control system trends of fan power or on/off status, or use data logger to monitor fan power for at least one week
Staged Control |  | Occupancy Sensor |  |  | Staged Control | as-Built sequence of operation | Occupancy Sensor
Other |  | On/Off |  |  | Other | as-Built sequence of operation | On/Off
DDC |  | Twist Timer |  |  | DDC | as-Built sequence of operation | Twist Timer
Electronic / Pneumatic |  | Manual |  |  | Electronic / Pneumatic | as-Built sequence of operation | Manual

## 6.9
SAMPLE FORM |  |  |  |  | SAMPLE FORM GUIDANCE
General Information |  |  |  |  | General Information
Site Name |  |  |  |  | Site Name | provide name of site |  | Fan Control
Exhaust/Return Fan ID/Tag |  |  |  |  | Fan ID/Tag | near fan nameplate, as-built fan schedule |  | Constant Air Volume | as-built sequence of operation
Location/Service |  |  |  |  | Location/Service | observe fan location/as-built fan schedule |  | VFD | as-built fan schedule
Year Built |  |  |  |  | Year Built | fan nameplate, as-built fan submittal |  | Discharge Damper | as-built sequence of operation, damper(s) located downstream of fan
Fan Data |  | Design/Operating Conditions |  |  | Fan Data
Manufacturer |  |  | Design | Measured | Manufacturer | fan nameplate, as-built fan schedule |  | Multi-Speed | as-built sequence of operation
Model Number |  | Total Static Pressure |  |  | Model Number | fan nameplate, as-built fan schedule |  | Staged Control | as-built sequence of operation
Serial Number |  | Occupied CFM |  |  | Serial Number | fan nameplate |  | Other | as-built sequence of operation
Fan Type / Size |  | Unoccupied CFM |  |  | Fan Type / Size | fan nameplate, as-built fan schedule |  | DDC | as-built sequence of operation
Fan Efficiency |  | Fan RPM |  |  | Fan Efficiency | fan nameplate, as-built fan schedule |  | Electronic Controls | as-built sequence of operation
|  | Volts | [5 empty] | Pneumatic Controls | as-built sequence of operation
Fan Motor Data |  | Occupied Amps |  |  | Fan Motor Data
Full Load HP |  | Unoccupied Amps | n/a |  | Full Load HP | motor nameplate, as-built motor submittal
Frame Size |  | Occupied kW |  |  | Frame Size | motor nameplate, as-built motor submittal
Enclosure Type |  | Unoccupied kW | n/a |  | Enclosure Type | motor nameplate, as-built motor submittal
Full Load RPM |  | Power Factor | n/a |  | Full Load RPM | motor nameplate, as-built motor submittal
Synch. RPM |  |  |  |  | Synch. RPM | motor nameplate, as-built motor submittal
Motor Efficiency |  |  |  |  | Motor Efficiency | motor nameplate, as-built motor submittal
Volts |  | Fan Control |  | Notes | Volts | motor nameplate, as-built motor submittal
Phase |  | Constant Air Volume |  | _____________________ | Phase | motor nameplate, as-built motor submittal
Full Load Amps |  | VFD |  | _____________________ | Full Load Amps | motor nameplate, as-built motor submittal
Motor In Exhaust Airflow? | Yes/No | Discharge Damper |  | _____________________ | Motor In Exhaust Airflow? | motor nameplate, as-built motor submittal
Drive Type |  | Multi-Speed |  | _____________________ | Drive Type | as-built fan schedule, as-built fan submittal
|  | Staged Control |  | _______________
Operating Schedule |  | Other |  | _____________________ | Operating Schedule
Always On |  | DDC |  | _____________________ | Always On | as-built sequence of operation, observe at least one week of control system trends of fan power or on/off status, or use data logger to monitor fan power for at least one week
Occupancy Sensor |  | Electronic Controls |  | _______________
On/Off Schedule |  | Pneumatic Controls |  | _____________________ | Occupancy Sensor | as-built sequence of operation, observe at least one week of control system trends of fan power with occupancy schedule, or use data logger to monitor fan power for at least one week with occupancy schedule
Controls Notes |  |  |  |  | On/Off Schedule | as-built sequence of operation, observe at least one week of control system trends of fan power or on/off status, or use data logger to monitor fan power for at least one week
Design/Operating Conditions
[6 empty] | Design | Measured
[5 empty] | Total Static Pressure | as-built fan schedule | test and balance report
[5 empty] | Occupied CFM | Basis of Design, as-built sequence of operation | building control system or logger trends
[5 empty] | Unoccupied CFM | Basis of Design, as-built sequence of operation | building control system or logger trends
[5 empty] | Fan RPM | as-built fan schedule | building control system or logger trends
[5 empty] | Volts | as-built fan schedule | building control system or logger trends
[5 empty] | Occupied Amps | as-built fan schedule | building control system or logger trends
[5 empty] | Unoccupied Amps | n/a | building control system or logger trends
[5 empty] | Occupied kW | as-built fan schedule | building control system or logger trends
[5 empty] | Unoccupied kW | n/a | building control system or logger trends
[5 empty] | Power Factor | n/a | building control system or logger trends

## 6.10
SAMPLE FORM |  |  |  | SAMPLE FORM GUIDANCE
General Information |  |  |  | General Information
Site Name |  |  |  | Site Name | provide name of site
Unit ID/Tag |  |  |  | Unit ID/Tag | near nameplate, as-built schedule
Location/Service |  |  |  | Location/Svce | facilities operator
Manufacturer |  |  |  | Manufacturer | nameplate, as-built schedule |  | Year Built | nameplate, as-built schedule
Model Number |  |  |  | Model Number | nameplate, as-built schedule |  | No. Zones Served by Unit | as-built mechanical drawings
Serial Number | Year Built: |  | No. of zones served by unit | Serial Number | nameplate
Unit Type | Condenser Type |  | Preheat/Heating Coil | Unit Type |  |  | Condenser Type |  | Preheat/Heating Coil
Rooftop Unit | Air-cooled |  | Water (HWS/HWR) (oF) | Rooftop Unit | observe location |  | Air-cooled | as-built submittal | HWS/HWR | as-built submittal
Split System | Water-cooled |  | Steam (psi) | Split System | observe; as-built drawings |  | Water-cooled | as-built submittal | Steam | as-built submittal
Window A/C | Evap-cooled |  | Electric (kW) | Window A/C | observe location |  | Evap-cooled | as-built submittal | Electric | as-built submittal
VAV | GSHP |  | Heating Capacity (MBH) | VAV | as-built submittal |  | GSHP | as-built submittal | Capacity | as-built submittal
CAV | WSHP |  | Fuel type________________ | CAV | as-built submittal |  | WSHP | as-built submittal | Fuel type | as-built submittal
Other _________ | Other________ |  |  | Other | as-built submittal |  | Other | as-built submittal
|  |  | Supply Fan Motor Data | [5 empty] | Supply Fan Motor Data
Compressor Data | Condenser Fan Data |  | Quantity | Compressor Data |  |  | Condenser Fan Data |  | Quantity | nameplate; as-built
Quantity | Quantity |  | Full Load HP | Quantity | count; as-built equip. schedule |  | Quantity | nameplate; as-built | Full Load HP | nameplate; as-built
RLA | Full Load Amps |  | Frame Size | RLA | nameplate; as-built submittal |  | Full Load Amps | nameplate; as-built | Frame Size | nameplate; as-built
Volts | Volts |  | Enclosure Type | Volts | nameplate; as-built submittal |  | Volts | nameplate; as-built | Enclosure Type | nameplate; as-built
Phase | Phase |  | Operating RPM | Phase | nameplate; as-built submittal |  | Phase | nameplate; as-built | Operating RPM | nameplate; as-built
Type | Nominal HP |  | Motor Efficiency | Type | nameplate; as-built submittal |  | Nominal HP | nameplate; as-built | Motor Efficiency | nameplate; as-built
|  |  | Volts | [5 empty] | Volts | nameplate; as-built
Supply Fan Data | Cooling Type |  | Phase | Supply Fan Data |  |  | Cooling Type |  | Phase | nameplate; as-built
Manufacturer | DX: Refrigerant Type |  | Full Load Amps | Manufacturer | nameplate; as-built submittal |  | Refrigerant Type | as-built submittal | Full Load Amps | nameplate; as-built
Model Number | Number of Circuits |  | Power Demand (kW) | Model Number | nameplate; as-built submittal |  | No. of Circuits | as-built submittal | Power Demand (kW) | control system/logger trends
Serial Number | CFM |  | Drive Type | Serial Number | nameplate; as-built submittal |  | CFM | as-built submittal | Drive Type | nameplate; as-built
Fan Type / Size | EDB/EWB (oF) |  |  | Fan Type/Size | nameplate; as-built submittal |  | EDB/EWB | as-built submittal
Fan Efficiency | LDB/LWB (oF) |  | Humidity Control NONE | Fan Efficiency | nameplate; as-built submittal |  | LDB/LWB | as-built submittal | Humidity Control
| Cooling Cap. (MBH) |  | Humidifier Type |  |  |  | Capacity | as-built submittal | Humidifier Type | as-built submittal
Supply Fan Control | EER |  | Humidity Sensor Location | Supply Fan Control |  |  | EER | as-built submittal | Sensor Location | SOO, observation
VFD | EER incl. evap. fan? | Y / N | RH Setpoint, Max | VFD | as-built sequence of operation; building control system or logger trends |  | Evap fan incl.? | as-built submittal | RH Setpoint, Max | as-built SOO
Discharge Damper |  |  | RH Setpoint, Min | Damper |  |  |  |  | RH Setpoint, Min | as-built SOO
Multi-Speed | Outside Air (OA) Control |  |  | Multi-Speed |  |  | Outside Air (OA) Control
DDC | Fixed OA CFM |  | Electrical Data | DDC |  |  | Fixed OA CFM | as-built SOO | Electrical Data
Pneumatic | Economizer? |  | MCA | Pneumatic |  |  | Economizer? | as-built SOO | MCA | nameplate; as-built
Room Thermostat | Minimum OA % |  | MOCP | Room T-stat |  |  | Minimum OA % | as-built SOO | MOCP | nameplate; as-built
Controls Notes |  |  |  | Controls Notes
Time of Day Scheduling __________________________________________________________________________ |  |  |  | Time of Day Scheduling |  | as-built sequence of operation, building control system or logger trends
___________________________________________________________________________________________ |  |  |  | Unit Staging |  | as-built sequence of operation, building control system or logger trends
___________________________________________________________________________________________
___________________________________________________________________________________________
Unit Staging ________________________________________________________________________________
___________________________________________________________________________________________
___________________________________________________________________________________________

## 6.11
SAMPLE FORM |  |  |  | SAMPLE FORM GUIDANCE
General Information |  |  |  | General Information |  | Information Location/Description
Site Name |  |  |  | Site Name | Enter the name of the building site/campus and building number (if applicable).
Equipment ID/Tag |  |  |  | Equipment ID/Tag | Enter the unit identifier, e.g. "CU-1."
Location/Service |  |  |  | Location/Service | Add any other information that helps identify what the system is serving.
Manufacturer |  |  |  | Manufacturer | Enter the unit manufacturer. Use nameplate or submittal data.
Model Number |  |  |  | Model Number | Enter the unit model number. Use nameplate or submittal data.
Associated Equipment |  |  |  | Associated Equipment | Enter the tag of the equipment served by the condensing unit/condenser.
Serial Number |  | Year Built |  | Serial Number | Enter the unit serial number. Use nameplate or submittal data.
|  |  |  | Year Built | Enter year of manufacture. Use nameplate or submittal data.
Type of Equipment |  | Condenser Fan Data |  | Type of Equipment |  |  | Condenser Fan Data
Condensing Unit |  | Quantity |  | Condensing Unit | nameplate; as-built submittal |  | Quantity | nameplate; as-built submittal
Condenser |  | Full Load Amps |  | Condenser | nameplate; as-built submittal |  | Full Load Amps | nameplate; as-built submittal
|  | Volts |  |  |  |  | Volts | nameplate; as-built submittal
Condenser Type |  | Phase |  | Condenser Type |  |  | Phase | nameplate; as-built submittal
Air-cooled |  | Nominal HP |  | Air-cooled | as-built submittal |  | Nominal HP | nameplate; as-built submittal
Evap-cooled |  | Fan Control | VFD / Single-speed / Two-Speed | Water-cooled | as-built submittal |  | Fan Control | nameplate; as-built submittal
Fluid-cooled |  |  |  | Evap-cooled | as-built submittal
Compressor Data |  | Electrical Data |  | Compressor Data | for condensing units only |  | Electrical Data
Quantity |  | Volts |  | Quantity | count; as-built equip. schedule |  | Volts | nameplate; as-built submittal
RLA |  | Phase |  | RLA | nameplate; as-built submittal |  | Phase | nameplate; as-built submittal
Volts |  | MCA |  | Volts | nameplate; as-built submittal |  | MCA | nameplate; as-built submittal
Phase |  | MOCP |  | Phase | nameplate; as-built submittal |  | MOCP | nameplate; as-built submittal
Type |  |  |  | Type | nameplate; as-built submittal
Cooling Type |  | Fluid-Cooled Data |  | Cooling Type |  |  | Fluid-Cooled Data | use only if condenser type is fluid-cooled
DX: Refrigerant Type |  | Fluid |  | DX: Refrigerant Type | as-built submittal |  | Fluid | nameplate; as-built submittal
Number of Circuits |  | GPM |  | Number of Circuits | as-built submittal |  | GPM | nameplate; as-built submittal
Cooling Cap. (MBH) |  | EWT/LWT (oF) |  | Cooling Cap. (MBH) | as-built submittal |  | EWT/LWT (oF) | nameplate; as-built submittal
EER/SEER |  | WPD (ft w.g) |  | EER/SEER | as-built submittal |  | WPD (ft w.g) | nameplate; as-built submittal
EER incl. supply fan? | Yes / No |  |  | EER incl. supply fan? | as-built submittal
Heat Pump? | Yes / No |  |  | Heat Pump? | as-built submittal
Heating Cap. (MBH) |  |  |  | Heating Cap. (MBH) | as-built submittal
HSPF/COP |  |  |  | HSPF/COP | as-built submittal
Controls Notes |  |  |  | Controls Notes
Time of Day Scheduling _______________________________________________________________________ |  |  |  | Time of Day Scheduling | as-built sequence of operation, building control system or logger trends
___________________________________________________________________________________________ |  |  |  | Unit Staging | as-built sequence of operation, building control system or logger trends
___________________________________________________________________________________________
___________________________________________________________________________________________
Unit Staging ________________________________________________________________________________
___________________________________________________________________________________________
___________________________________________________________________________________________

## 7.0
SAMPLE FORM | [5 empty] | SAMPLE FORM GUIDANCE
General Information | [5 empty] | General Information
Site Name | [5 empty] | Site Name | Provide name of site
Location of Pool | [5 empty] | Location of Pool | Observe location in relation to building
Size (gallons) |  | Surface Area |  |  |  | Size (gallons) | as-built plans or direct measurement | Surface Area | as-built plans or direct measurement
Activity Schedule |  | Year Built |  |  |  | Activity schedule | Indicate what pool is used for (recreation, teaching, training, etc) and typical weekly schedule | Year Built | as-built plans or submittals
Outdoor Conditions |  | Heating Conditions |  |  |  | Outdoor Conditions |  | Heating Conditions
Avg temp for coldest month of use |  | Heating Method |  |  |  | Avg temp for coldest month of use | ASHRAE Fundamentals | Heating Method | as-built submittal
Saturation vapor pressure |  | Cover Type |  |  |  | Saturation vapor pressure | ASHRAE Fundamentals | Cover Type | as-built submittal
Atmospheric pressure |  | Cover U-value |  |  |  | Atmospheric pressure | ASHRAE Fundamentals | Cover U-value | as-built submittal
Wind speed |  | Cover Schedule |  |  |  | Wind speed | ASHRAE Fundamentals | Cover Schedule | interview facilities staff
Annual Solar Radiation |  | Desired Water Temp |  |  |  | Annual Solar Radiation | ASHRAE Fundamentals | Desired Water Temp | as-built sequence of operations
% Shaded area in pool area |  | Measured Water Temp |  |  |  | % Shaded area in pool area | Estimate avg. percentage based on observations throughout one day | Meas Water Temp | control system or direct measurement
|  | Warm up time | [5 empty] | Warm up time | control system, interview staff
Indoor Conditions | [5 empty] | Indoor Conditions
Room Temp Setpoint |  | Heating Schedule_______________________________________ |  |  |  | Room Temp Setpoint | as-built sequence of operations | Heating Schedule | as-built sequence of operations, control system, and interview staff; obtaining annual hours of heating is desired, how is it controlled?
Room RH Setpoint | [5 empty] | Room RH Setpoint | as-built sequence of operations
Method of Air Delivery | [5 empty] | Method of Air Delivery | as-built sequence of operations
|  | Gas Pool Heaters | [5 empty] | Gas Pool Heaters
Filter Pump Data |  | Capacity |  |  |  | Filter Pump Data |  | Capacity | as-built submittal
Filter Type |  | Fuel Type |  |  |  | Filter Type | as-built submittal | Fuel Type | as-built submittal
Filter Pressure Drop |  | Efficiency |  |  |  | Filter Pressure Drop | as-built submittal | Efficiency | as-built submittal
Power Demand (kW) |  | Power Demand (kW) |  |  |  | Power Demand | control system, logger trends | Power Demand | control/logger trends; spot measure
Hours on per day | [5 empty] | Hours on per day | control system, logger trends
VFD | yes/no | Heat Pump Pool Heaters |  |  |  | VFD | as-built submittal | Heat Pump Pool Heaters
|  | Capacity | [5 empty] | Capacity | as-built submittal
Solar Pool Heaters |  | Air/Water Source |  |  |  | Solar Pool Heaters |  | Air/Water Source | as-built submittal
Total Collector Area |  | COP |  |  |  | Total Collector Area | as-built submittal | COP | as-built submittal
Collector Orientation/Tilt |  | Compressor Type |  |  |  | Collector Orientation/Tilt | observe/measure | Compressor Type | as-built submittal
Collector Type |  | Refrigerant Type |  |  |  | Collector Type | as-built submittal | Refrigerant Type | as-built submittal
Distance from pool to collectors |  | Power Demand (kW) |  |  |  | Distance from pool to collectors | as-built plans or measure | Power Demand | control/logger trends; spot measure
Pumping power per collector area | [5 empty] | Pumping power per collector area | as built submittal
Heat Exchanger Effectiveness |  | Pool Accessories |  | Power Demand | Hours on per day | Heat Exchanger Effectiveness | as built submittal | Pool Accessories |  | Power Demand | Hrs on per day
|  | Ozone Generator | yes/no |  |  |  |  | Ozone Generator | as-built schedules, observe if present | submittals, also recommend measuring actual kW use | control system, logger trends
|  | Oxygen Concentrator | yes/no |  |  |  |  | Oxygen Concentrator
|  | Air Compressors | yes/no |  |  |  |  | Air Compressors
Additional Notes/Comments | [5 empty] | Additional Notes/Comments

## 7.1
SAMPLE FORM |  |  | SAMPLE FORM GUIDANCE
General Information |  |  | General Information
Site Name |  |  | Site Name | provide name of site
Room Name |  |  | Room Name | provide name of kitchen room
Location/Service |  |  | Location/Service | facilities operator
Year Built | Floor Area (sq. ft.) |  | Year Built | as-built drawings, facilities operator | Floor Area | measure from as-built floor plans
Oven Data | Other Equipment Data |  | Oven Data |  | Other Equipment Data
Quantity | Equipment Type |  | Quantity | count at site | Equipment Type | nameplate, as-built submittal
Manufacturer | Quantity |  | Manufacturer | nameplate, as-built oven submittal | Quantity | nameplate, as-built submittal
Model Number | Manufacturer |  | Model Number | nameplate, as-built oven submittal | Manufacturer | nameplate, as-built submittal
Capacity | Model Number |  | Capacity | nameplate, as-built oven submittal | Model Number | nameplate, as-built submittal
Fuel Type | Power Demand (kW) |  | Fuel Type | nameplate, as-built oven submittal | Power Demand (kW) | building control system or logger trends
Efficiency | Hours On per Day |  | Efficiency | nameplate, as-built oven submittal, compute from building control system or logger trends | Hours On per Day | building control system or logger trends
Power Demand (kW) | Year Installed |  |  |  | Year Installed | nameplate, as-built submittal
Hours On per Day | Energy Star Rated? | Yes/No | Power Demand (kW) | if electric, building control system or logger trends
Year Installed
|  |  | Hours On per Day | building control system or logger trends
Refrigerator Data | Motor Data |  | Year Installed | nameplate, as-built oven submittal
Quantity | Quantity
Manufacturer | Full Load HP |  | Refrigerator Data |  | Motor Data
Model Number | Frame Size |  | Quantity | count at site | Quantity | nameplate, as-built submittal
Capacity | Enclosure Type |  | Manufacturer | nameplate, as-built refrigerator submittal | Full Load HP | nameplate, as-built submittal
Compressor Type | Operating RPM |  | Model Number | nameplate, as-built refrigerator submittal | Frame Size | nameplate, as-built submittal
Efficiency | Motor Efficiency |  | Capacity | nameplate, as-built refrigerator submittal | Enclosure Type | nameplate, as-built submittal
Power Demand (kW) | Volts |  | Compressor Type | nameplate, as-built refrigerator submittal | Operating RPM | building control system or logger trends
Hours On per Day | Phase |  | Efficiency | nameplate, as-built refrigerator submittal | Motor Efficiency | nameplate, as-built submittal
Year Installed | Full Load Amps |  | Power Demand (kW) | building control system or logger trends | Volts | building control system or logger trends
| Power Demand (kW) |  | Hours On per Day | building control system or logger trends | Phase | building control system or logger trends
Compressor Data | Drive Type |  | Year Installed | nameplate, as-built refrigerator submittal | Amps | building control system or logger trends
Quantity | Hours On per Day |  |  |  | Power Demand (kW) | building control system or logger trends
Capacity | Year Installed |  | Compressor Data |  | Drive Type | nameplate, as-built submittal
Manufacturer |  |  | Quantity | count at site | Hours On per Day | building control system or logger trends
Model Number |  |  | Capacity | nameplate, as-built compressor submittal | Year Installed | nameplate, as-built submittal
Type | Room Conditions |  | Manufacturer | nameplate, as-built compressor submittal
Efficiency | Room Temp Setpt (heat/cool) |  | Model Number | nameplate, as-built compressor submittal | Room Conditions
Power Demand (kW) | Cooling System Type |  | Type | nameplate, as-built compressor submittal | Room Temperature | building control system or logger trends
Hours On per Day | Air Delivery System Type |  | Efficiency | nameplate, as-built compressor submittal | Cooling System | as-built mechanical drawings
Year Installed | Heating System Type |  | Power Demand (kW) | building control system or logger trends | Air Delivery System | as-built mechanical drawings
|  |  | Hours On per Day | building control system or logger trends | Heating System | as-built mechanical drawings
|  |  | Year Installed | nameplate, as-built compressor submittal
Controls Notes | Range Hoods |  |  |  | Range Hoods
Time of Day Scheduling | Quantity |  | Controls Notes |  | Quantity | count; as-built equipment schedule
| Type |  | Time of Day Scheduling |  | Type | e.g. condensate, grease; as-built submittal
| Max/Min CFM |  | as-built sequence of operation, control system or logger trends of equipment power demand (kW) (or Amps)
| Control Method |  |  |  | Max/Min CFM | as-built submittal; spot measurement or control system/logger trends
[5 empty] | Control Method | as-built sequence of operation

## 7.2
SAMPLE FORM | [8 empty] | SAMPLE FORM GUIDANCE
General Information | [8 empty] | General Information
Site Name | [8 empty] | Site Name | Provide name of site
Room Name | [8 empty] | Room Name & Area | Provide name of room
Floor Area (sf) | [8 empty] | Floor Area | as-built floor plan
Airflow Determinant | [8 empty] | Airflow Determinant | Is airflow supplied to the room dominated by ventilation, exhaust, or cooling requirements? Refer to as-built room plans or basis of design
Ventilation Data |  |  | Exhaust Data
CAV/VAV |  |  |  | Quantity | VAV / CAV | Min Airflow | Max Airflow | Time of Day Scheduling | Ventilation Data |  | Exhaust Data
Occupied ACH | [8 empty] | CAV/VAV | submittals/trend data |  | Qty | VAV / CAV | Min Airflow | Max Airflow | Time of Day Scheduling
Unoccupied ACH |  |  | Fume Hoods | [5 empty] | Occupied ACH | submittals/trend data
Particle Counting | yes / no |  | Snorkels | [5 empty] | Unoccupied ACH | submittals/trend data | Fume Hoods | as-built equipment submittal | as-built equipment submittal, also look at control system or logger trends to verify | as-built equipment submittal, also look at control system or logger trends to verify | as-built equipment submittal, also look at control system or logger trends to verify | as-built sequence of operations, also look at control system or logger trends to verify
Contaminant Sensors | yes / no |  | Gas Cabinets | [5 empty] | Particle Counting | submittals/trend data | Snorkels
Occ. Sensors | yes / no |  | BS Cabinets | [5 empty] | Cont. Sensors | submittals/trend data | Gas Cabinets
CO2 Sensors | yes / no |  | Other | [5 empty] | Occ. Sensors | submittals/trend data | BS Cabinets
[9 empty] | CO2 Sensors | submittals/trend data | Other
Equipment Data |  |  | Low Pwr/ Standby Mode W |  |  |  | Time of Day Sched | Other Efficiency Features
Tag ID & type | Mfr / Model | NP Pwr Rating |  | Active Mode W | Cooling Req't | Typ hr/week |  |  | Equipment Data
[9 empty] | Tag ID & type | Near equipment nameplate or as-built equipment schedule for tag ID. List all types of lab equipment in room including but not limited to: autoclaves, freezers, refrigerators, ovens, lasers, spectrometers, cage washers, centrifuges, glove boxes, vacuum pumps, chromatographs, cryo coolers, dry baths, glass washers, growth chambers, heat blocks, incubators, and thermal cyclers.
[9 empty] | Mfr / Model | Nameplate or as-built equipment submittal
[9 empty] | Nameplate Pwr Rating | Nameplate or as-built equipment submittal
[9 empty] | Low Pwr/Standby Mode W | logger trends, also see if this is specified in equipment submittal
[9 empty] | Active Mode W | logger trends, also see if this is specified in equipment submittal
[9 empty] | Cooling Req't | as-built equipment submittal
[9 empty] | Typ hr/week | interview lab users to quantify typical usage, also use data logger to monitor power for at least one week
[9 empty] | Time of Day Scheduling | interview lab users, logger trends
[9 empty] | Other Efficiency Features | as-built equipment submittal, also interview lab users to see if there any energy saving opportunities in behavioral habits

## 7.3
SAMPLE FORM |  | SAMPLE FORM GUIDANCE
General Information |  | General Information
Site Name |  | Site Name | provide name of site
Room/Area Name |  | Room Name | provide name of conditioned room or area
Location/Service |  | Location/Service | provide are served; from facilities operator
Conditioned Floor Area (sq. ft.) |  | Floor Area | measure from as-built floor plans
Compressor Data | Evaporator Coil Data | Compressor Data |  | Evaporator Coil Data
Manufacturer | Manufacturer | Manufacturer | nameplate; as-built submittal | Manufacturer | nameplate; as-built submittal
Type | Type | Type | nameplate; as-built submittal | Type | nameplate; as-built submittal
Quantity | Coil Quantity | Quantity | count; as-built equipment sched | Coil Quantity | nameplate; as-built equipment sched
Model Number | Model Number | Model Number | nameplate; as-built submittal | Model Number | nameplate; as-built submittal
Serial Number(s) | Serial Number(s) | Serial Number(s) | nameplate | Serial Number(s) | nameplate
Tag Number | Tag Number | Tag Number | located near nameplate | Tag Number | located near nameplate
Refrigerant Type | Suction Group | Refrigerant Type | nameplate; as-built submittal | Suction Group | nameplate; as-built submittal
Suction Press/Temp | Location | Suction Press/Temp | nameplate; as-built submittal | Location | observe; as-built submittal
Discharge Press/Temp | Room Temperature | Discharge Press/Temp | nameplate; as-built submittal | Room Temperature | control system or logger trends
Capacity (MBH) | Defrost Type | Capacity (MBH) | nameplate; as-built submittal | Defrost Type | as-built submittal
Power Demand (kW) | Defrost Duration | Power Demand (kW) | control system or logger trends | Defrost Duration | control system or logger trends
Hours On per Day | Number of Defrost/day | Hours On per Day | control system or logger trends | Number of Defrost/day | control system or logger trends
Year Installed | Defrost Power Draw (kW) | Year Installed | nameplate; as-built submittal | Defrost Power Draw (kW) | control system or logger trends
Condenser Data | Evaporator Fan Data | Condenser Data |  | Evaporator Fan Data
Manufacturer | Manufacturer | Manufacturer | nameplate; as-built submittal | Manufacturer | nameplate; as-built submittal
Type | Quantity | Type | nameplate; as-built submittal | Serial Number(s) | nameplate
Quantity | Model Number | Quantity | count; as-built equipment sched | Model Number | nameplate; as-built submittal
Model Number | Serial Number(s) | Model Number | nameplate; as-built submittal | Serial Number | nameplate
Serial Number(s) | Fan Type / Size | Serial Number(s) | nameplate | Fan Type / Size | nameplate; as-built submittal
Tag Number | Fan Efficiency | Tag Number | located near nameplate | Fan Efficiency | nameplate; as-built submittal
Capacity (MBH) |  | Capacity (MBH) | nameplate; as-built submittal
Fan Motor HP | Evaporator Fan Motor Data | Fan Motor HP | nameplate; as-built submittal | Evaporator Fan Motor Data
Fan Motor Efficiency | Fan Motor HP | Fan Motor Efficiency | nameplate; as-built submittal | Fan Motor HP | nameplate; as-built submittal
Fan Motor Quantity | Fan Motor Efficiency | Fan Motor Quantity | count; as-built equipment sched | Fan Motor Efficiency | nameplate; as-built submittal
Fan Amps / Volts / f | Fan Motor Quantity | Fan Amps / Volts / f | nameplate; as-built submittal | Fan Motor Quantity | count; as-built equipment sched
Fan Power Draw (kW) | Fan Amps / Volts / f | Fan Power Draw (kW) | control system or logger trends | Fan Amps / Volts / f | nameplate; as-built submittal
Year Fan Installed | Fan Power Draw (kW) | Year Fan Installed | nameplate; as-built submittal | Fan Power Draw (kW) | control system or logger trends
Pump Motor HP | Year Fan Installed | Pump Motor HP | nameplate; as-built submittal | Year Fan Installed | nameplate; as-built submittal
Pump Motor Efficiency | Drive Type | Pump Motor Efficiency | nameplate; as-built submittal | Drive Type | as-built submittal
Pump Motor Quantity |  | Pump Motor Quantity | count; as-built equipment sched
Pump Amps / Volts / f | Controls | Pump Amps / Volts / f | nameplate; as-built submittal | Controls
Pump Power Draw (kW) | Conditioned Area Enclosed? | Pump Power Draw (kW) | control system or logger trends | Conditioned Area Enclosed? | observe; e.g. strip curtains, enclosing doors
Year Pump Installed |  | Year Pump Installed | nameplate; as-built submittal
Controls Notes |  | Controls Notes
Time of Day Scheduling |  | Time of Day Scheduling | as-built sequence of operation, control system or logger trends of equipment power demand (kW) (or Amps)
Heat Recovery? |  | Heat Recovery? | describe type of heat recovery employed

## 7.4
SAMPLE FORM |  |  |  |  | SAMPLE FORM GUIDANCE
General Information |  |  |  |  | General Information |  | Fan Control
Site Name |  |  |  |  | Site Name | provide name of site | Constant Air Volume | as-built sequence of operation
Room Name |  |  |  |  | Room Name | provide name of datacenter or IT room | VFD | inside CRAH unit
Location/Service |  | Total Floor Area (sf) |  |  | Location/Service | facilities operator | Multi-Speed | as-built motor submittal
Year Built |  | Total Server Load (kW) |  |  | Year Built | as-built drawings, facilities operator | Connected to DDC? | as-built sequence of operation
[5 empty] | Total Floor Area | as-built floor plans
CRAC/CRAH Units - General |  | Design/Operating Conditions |  |  | Total Server Load | measure with power meter | Humidity Control
Quantity |  |  | Design | Measured |  |  | Humidifier Type | as-built humidifier schedule
Nominal Capacity |  | PUE |  |  | CRAC/CRAH Units - General |  | Humidity Sensor Location | as-built sequence of operation, visual observation
Compressor Type |  | Total Static Pressure |  |  | Quantity | count at site
|  | Supply CFM |  |  | Nominal Capacity | as-built CRAC/H schedule | RH Setpoint, Max | % or dewpoint; as-built sequence of operation, control system or logger trends
CRAC/CRAH Fan Data |  | Fan RPM |  |  | Compressor Type | DX or CHW plant, as-built CRAC/H schedule
Manufacturer |  | Volts |  |  |  |  | RH Setpoint, Min | % or dewpoint; as-built sequence of operation, control system or logger trends
Model Number |  | Amps |  |  | CRAC/CRAH Fan Data
Serial Number(s) |  | Fan Power Demand (kW) |  |  | Manufacturer | as-built CRAC/H schedule | Transformers
Fan Type / Size |  | Power Factor | n/a |  | Model Number | as-built CRAC/H schedule | Quantity | as-built electrical line diagram
Fan Efficiency |  | Return Air Temperature |  |  | Serial Number(s) | as-built CRAC/H schedule | Capacity | as-built transformer submittal
|  | Supply Air Temperature |  |  | Fan Type / Size | as-built CRAC/H schedule | Manufacturer | nameplate
CRAC/CRAH Fan Motor Data |  |  |  |  | Fan Efficiency | as-built CRAC/H schedule | Model Number | nameplate
Full Load HP |  | Fan Control |  |  |  |  | Oper Output Power | measure with power meter
Frame Size |  | Constant Air Volume |  |  | CRAC/CRAH Fan Motor Data |  | Oper Input Power | measure with power meter
Enclosure Type |  | VFD |  |  | Full Load HP | motor nameplate, as-built CRAC/H schedule | Operating Load (%) | output power ÷ capacity
Motor Efficiency |  | Multi-Speed |  |  | Frame Size | motor nameplate, as-built CRAC/H schedule | Equipment Served | as-built electrical line diagram
Motor In Supply Airflow? | Yes/No | Connected to DDC? |  |  | Enclosure Type | motor nameplate, as-built CRAC/H schedule
Drive Type |  |  |  |  | Motor Efficiency | motor nameplate, as-built motor submittal | Uninterruptible Power Supply
|  | Humidity Control |  |  | Motor in Supply Airflow? | motor nameplate, as-built motor submittal | Quantity | as-built electrical line diagram
Configuration |  | None |  |  | Drive Type | as-built fan schedule, as-built fan submittal | Capacity | as-built transformer submittal
Open, No Hot/Cold Aisles |  | Humidifier Type |  |  |  |  | Manufacturer | nameplate
Open Hot/Cold Aisle |  | Humidity Sensor Location |  |  | Configuration |  | Model Number | nameplate
Hot/Cold Aisle w/ Ducted Return |  | RH Setpoint, Max |  |  | Open, No Hot/Cold | observe server racks | Oper Output Power | measure with power meter
Fully Enclosed Hot/Cold Aisles |  | RH Setpoint, Min |  |  | Open Hot/Cold Aisle | observe server aisles, measure temperatures in aisles | Oper Input Power | measure with power meter
[7 empty] | Operating Load (%) | output power ÷ capacity
Uninterruptible Power Supply |  | Transformers |  |  | Hot/Cold Aisle w/ Ducted Return | observe server aisles and ducting to return opening in CRAC/CRAHs, measure temperatures in aisles | Equipment Served | as-built electrical line diagram
Quantity |  | Quantity
Capacity |  | Capacity |  |  | Fully Enclosed Hot/Cold Aisles | observe server aisles and enclosure at tops and ends of aisles, measure temperatures in aisles | Air Side Economizing
Manufacturer |  | Manufacturer |  |  |  |  | Economizer Control | e.g. drybulb, RH, or enthalpy; as-built sequence of operation, control system trends
Model Number |  | Model Number
Operating Output Power |  | Operating Output Power |  |  | Design/Operating Conditions |  | Economizer Upper Limit | e.g. upper OA drybulb temp lockout; as-built sequence of operation, control system trends
Operating Input Power |  | Operating Input Power |  |  | Design | as-built CRAC/CRAH schedule
Operating Load Factor (%) |  | Operating Load Factor (%) |  |  | Measured | building control system or logger trends | Economizer Lower Limit | e.g. lower OA drybulb temp lockout; as-built sequence of operation, control system trends
Equipment Served |  | Equipment Served
[5 empty] | Controls Notes |  | Economizer Control Point | e.g. return air drybulb temp; as-built sequence of operation
Controls Notes |  | Air Side Economizing | Yes/No |  | Server Operation/ HVAC Schedule | as-built sequence of operation, building control system or logger trends
Server Operation/HVAC System Schedule |  | Economizer Control
|  | Economizer Upper Limit |  |  | CRAC/CRAH Staging | as-built sequence of operation, building control system or logger trends
CRAC/CRAH Staging |  | Economizer Lower Limit
Economizer Control Point

## 7.5
SAMPLE FORM |  |  |  |  | SAMPLE FORM GUIDANCE
General Information |  |  |  |  | General Information
Site Name |  |  |  |  | Site Name | Provide name of site
Location/Service |  |  |  |  | Location/Service | observe location and purpose of process equipment
Year Built |  |  |  |  | Year Built | as-built drawings, equipment submittals
Compressed Air System |  | Compressed Air Design / Operating Conditions |  |  | Compressed Air System |  | Compressed Air Design/Oper Conditions
Type of Compressor |  |  | Required | Measured | Type of Compressor | as-built submittal |  | Required | Measured
Compressor Efficiency |  | Flow rate |  |  | Compressor Efficiency | as-built submittal | Flow rate | as-built schedule | control system or logger trends
Compressor Controls |  | Pressure |  |  | Compressor Controls | as-built sequence of operations | Pressure
Quantity of Filters |  | Dew Point |  |  | Quantity of Filters | as-built schedule | Dew Point
Filter Type |  | Hrs on per day |  |  | Filter Type | as-built submittal
Filter Pressure Drop |  | Compressor Power Demand |  |  | Filter Pressure Drop | as-built submittal | Pressure / Flow Controller? |  | as-built schedule
After cooler Effectiveness |  | Pressure / Flow Controller? |  | yes / no | After cooler Effectiveness | as-built submittal | Leaks Detected? |  | Visual inspection and interview facilities staff
Condensate Separation Efficiency |  | Leaks Detected? |  | yes / no | Condensate Separation Efficiency | as-built submittal | If so, where?
Dryer Size |  | If so, where? |  |  | Dryer Size | as-built submittal
Dryer Efficiency |  |  |  |  | Dryer Efficiency | as-built submittal | Uses of Compressed Air System:
Dryer Pressure Drop |  | Uses of Compressed Air System: |  |  | Dryer Pressure Drop | as-built submittal | as-built schedule, and floor plans, also interview facilities staff to ensure there are not inappropriate uses of compressed air (i.e. diaphragm pumps, pneumatic controls, etc)
Dryer Purge Rate |  |  |  |  | Dryer Purge Rate | as-built submittal
Dryer Purge Rate Control |  |  |  |  | Dryer Purge Rate Control | as-built sequence of operations
Receiver Tank Size |  |  |  |  | Receiver Tank Size | as-built schedule
Receiver Tank Location |  |  |  |  | Receiver Tank Location | as-built floor plans
Central Vacuum System |  | Central Vacuum Design / Operating Conditions |  |  | Central Vacuum System |  | Central Vacuum Design/Oper Conditions
Type of Pumps |  |  | Required | Measured | Type of Pumps | as-built submittal |  | Required | Measured
Quantity of Pumps |  | Flow rate |  |  | Quantity of Pumps | as-built schedule | Flow rate | as-built schedule | control system or logger trends
Pump Controls |  | Pressure |  |  | Pump Controls | as-built sequence of operations | Pressure
Uses of Central Vacuum System: |  | Hrs on per day |  |  | Uses of Central Vacuum System:
|  | Pump Power Demand |  |  | as-built schedule, and floor plans, also interview facilities staff |  | Leaks Detected? |  | Visual inspection and interview facilities staff
|  | Leaks Detected? |  | yes/no |  |  | If so, where?
If so, where?
Process Chilled Water System |  | Chilled Water Design / Operating Conditions |  |  | Process Chilled Water System |  | Chilled Water Design/Oper Conditions
Portable Process Chillers | yes / no |  | Required | Measured | Portable Process Chillers | as-built schedule |  | Required | Measured
Separate High Temp Chiller plant | yes / no | Flow rate |  |  | Separate High Temp Chiller plant | as-built schedule | Flow rate | as-built schedule | control system or logger trends
Low Temp Chiller plant w/ mixing loop | yes / no | Head |  |  | Low Temp Chiller plant w/ mixing loop | as-built schedule | Head | as-built schedule
Water Side Free Cooling | yes / no | Supply Temp |  |  | Water Side Free Cooling | as-built schedule | Supply Temp | as-built schedule
note: circle all that apply
Uses of Process Chilled Water: |  |  |  |  | Uses of Process Chilled Water:
as-built schedule, and floor plans, also interview facilities staff
Elevators |  | Elevator Design / Operating Conditions |  |  | Elevators |  | Elevator Design/Oper Conditions
Capacity (lbs) |  |  | Rated | Measured | Capacity (lbs) | as-built submittal |  | Rated | Measured
Year Built |  | Speed |  |  | Year Built | as-built submittal | Speed | as-built submittal | control system or logger trends
Type (hydraulic, traction, etc) |  | Riding Power |  |  | Type (hydraulic, traction, etc) | as-built submittal | Riding Power
Frequency of Use |  | Standby Power |  |  | Frequency of Use | control system or logger trends | Standby Power
Machine Room Cooling Load |  |  |  |  | Machine Room Cooling Load | as-built submittal